ERCOT Operations Report

September 2007 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration |  |
| --- | --- | --- | --- |
| 9/5/2007 7:53 | 59.739 | 3 m | 2 units totaling 1084 MW tripped |
| 9/5/2007 8:00 | 60.145 | 2 m 16 s | Overshoot from trips |
| 9/6/2007 23:09 | 60.117 | 7 m 40 s | 1000 + SCE corrected over 23:00 ramp that had a 2470 MW schedule change. |
| 9/10/2007 13:05 | 59.882 | 6 s | 4 unit train totaling 725 MW tripped |
| 9/18/2007 23:04 | 59.899 | 4 s | 3200 MW schedule change. |
| 9/20/2007 1:46 | 59.795 | 1 m 8 s | 500 MW trip. |
| 9/24/2007 5:56 | 60.109 | 40 s | 2660 schedule change. |
| 9/26/2007 0:08 | 60.105 | 1 m 14 s | 2240 schedule change |

Deployed Responsive (Reported Above)

| ID | Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- | --- |
| 1 | 9/2 16:35:24 | 9/2 16:45:58 | 0:10:34 | 315 | STLF error |
| 2 | 9/4 21:29:58 | 9/4 21:42:38 | 0:12:40 | 310 | SCE |
| 3 | 9/5 6:17:34 | 9/5 6:32:46 | 0:15:12 | 315 | SCE |
| 4 | 9/5 7:53:02 | 9/5 8:19:58 | 0:26:56 | 1162 |  |
| 5 | 9/6 17:12:00 | 9/6 17:28:36 | 0:16:36 | 315 | Units Tripped |
| 6 | 9/10 13:05:36 | 9/10 13:30:58 | 0:25:22 | 448 |  |
| 7 | 9/16 0:33:12 | 9/16 0:49:32 | 0:16:20 | 420 | Schedule change |
| 8 | 9/18 23:04:34 | 9/18 23:16:28 | 0:11:54 | 361 |  |
| 9 | 9/20 1:46:02 | 9/20 2:15:30 | 0:29:28 | 890 |  |
| 10 | 9/21 9:42:00 | 9/21 9:49:10 | 0:07:10 | 351 | Unit Trip |
| 11 | 9/23 23:21:46 | 9/23 23:30:00 | 0:08:14 | 310 | Offset |
| 12 | 9/23 23:59:34 | 9/24 0:08:43 | 0:09:09 | 310 | Schedule change |
| 13 | 9/25 23:01:14 | 9/25 23:11:06 | 0:09:52 | 310 | Schedule change |
| 14 | 9/26 16:05:58 | 9/26 16:19:46 | 0:13:48 | 326 | Unit Trip |
| 15 | 9/27 20:02:20 | 9/27 20:10:08 | 0:07:48 | 351 | Unit Trip |
| 16 | 9/29 14:13:56 | 9/29 14:28:40 | 0:14:44 | 336 | Unit Trip |
| 17 | 9/30 11:19:04 | 9/30 11:43:44 | 0:24:40 | 326 | Offset |

DayAhead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin |  | 3 | 28 | 31 |
| Bryan Area |  |  |  |  |
| Corpus |  |  | 7 | 7 |
| DFW |  | 19 | 2 | 21 |
| E RIO |  |  | 2 | 2 |
| Houston |  |  | 15 | 15 |
| Laredo | 90 |  |  | 90 |
| North |  | 8 | 46 | 54 |
| Northeast |  |  |  |  |
| San Antonio |  |  | 11 | 11 |
| South |  |  | 3 | 3 |
| W RIO |  |  |  |  |
| Western |  |  | 1 | 1 |
|  | 90 | 30 | 115 | 235 |

| Historical Totals | Sept-06 | Aug-07 | Sept-07 |
| --- | --- | --- | --- |
| Austin | 0 | 16 | 31 |
| Bryan Area | 14 | 0 | 0 |
| Corpus | 6 | 1 | 7 |
| DFW | 19 | 23 | 21 |
| E RIO | 5 | 1 | 2 |
| Houston | 2 | 13 | 15 |
| Laredo | 90 | 92 | 90 |
| North | 0 | 91 | 54 |
| Northeast | 0 | 2 | 0 |
| San Antonio | 0 | 18 | 11 |
| South | 0 | 0 | 3 |
| W RIO | 65 | 0 | 0 |
| Western | 8 | 2 | 1 |
| Total | 209 | 259 | 235 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple - Tradinghouse & Temple Switch - Lake Creek 345 kV | Temple Pecan Creek - Lake Creek 138 kV | 17 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Nacogdoches 345/138 kV Auto 1 | 8 |
| Monticello - Farmersville 345 kV | Monticello - Sulfur Springs Switch 345 kV | 7 |
| Lytton Springs-Zorn & Austrop-Zorn | Canyon - Rohr 138 kV | 6 |
| Midland East - Odessa EHV 345 kV | Moss Switch - Odessa Southwest | 5 |
| Trinidad - Stryker Creek & Enterprise | Athens Tap - Elkton 138 kV | 5 |
| Trinidad - Stryker Creek & Enterprise | Athens Tap - Athens North Switch 138 kV | 4 |
| South Lane City - Lane City 138 kV | South Lane City - New Gulf 138 kV | 4 |
| Marion - Zorn & Clear Springs | Seguin - Seguin West 138 kV | 3 |
| Austrop 345/138 kV Auto #2 | Austrop 345/138 kV Auto #1 | 2 |
| Austrop -Garfiled & Zorn 345 kV | Austrop 345/138 kV Auto #1 | 2 |
| Trinidad - Stryker Creek & Enterprise | Stryker Creek - Cherokee POI 138 kV | 2 |
| Trinidad - Richland Chambers 345 kV | Big Brown SES - Jewett 345 kV | 2 |
| Big Brown SES - Jewett 345 kV | Big Brown SES - Jewett 345 kV | 2 |
| Menard - Gillespie 138 kV | Menard 138/69 kV Auto | 2 |
| Friend Ranch 138/69 kV Auto | Sonora 138/69 kV Auto | 2 |
| Holly - Barney Davis 138 kV | Cabaniss - Westside 138 kV | 2 |
| Big Brown - Richland Chambers | Trinidad SES 345/138 kV Auto | 1 |
| Collin - Anna Switch 345 kV | Payne Switch - Alla Hubbard 138 kV | 1 |
| Fisher Road -Oklaunion & Bowman | Graham SES - Long Creek 345 kV | 1 |
| Allen - Renner & P.Tennyson 345 kV | Allen Switch - Ben Davis 138 kV | 1 |
| Gibbons Creek - Twin Oaks 345 kV | Robinson - Watson Chapel 138 kV | 1 |
| King - Kuykendahl - Roans Priaire & Jewett - Tomball 345 kV | Big Brown SES - Jewett 345 kV | 1 |
| North Edinburg - Rio Hondo 345 kV | South McAllen - Las Milpas 138 kV | 1 |
| Oasis - PH Robinson 345 kV | Garrott - Kirby 138 kV | 1 |
| Renner Switch - Farmersville | Anna Switch - Collin 345 kV | 1 |
| San Miguel 138/69 kV | Derby - Pearsall 69 kV | 1 |
| Snyder - Sun Switch 138 kV | Ennis Creek Switch 138/69 kV Auto | 1 |
| Tradinghouse - Venus 345 kV | Big Brown SES - Jewett 345 kV | 1 |
| West Levee Switch 345/138 kV Auto | West Levee 345/138 kV Auto #2 | 1 |
| Trinidad - Watermill Switch & Tricorner | Trinidad SES 345/138 kV Auto | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North - Houston | 6 |
| West - North | 1 |
| North - West | 1 |

New RAP

None.

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 09/27/2007 | Day Ahead Desk V3R34 | 349 |
| 09/17/2007 | Shift Supervisor, V3R41 | 348 |
| 09/17/2007 | Transmission & Security Desk, V3R87 | 347 |
| 09/17/2007 | Frequency Control Desk, V3R58 | 346 |

## Blackout/Load Shed Incidences

None

EECP

9/5	Initiated EECP step 1 from 08:04 to 09:33

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

9/13	Ability to independently enable/disable SPS for RTCA and VSAT migrated into production.

9/20	Replacement Reserve Service failed to clear for 9/21

9/22	Replacement Reserve Service failed to clear for 9/23

Communication

9/4	Held intervals 10:15 and 10:30.  Offset error.

9/19	Held interval 00:15.  Offset error.

## ERCOT peak (Unofficial)

9/07 	17:00	55,000

Yearly MTLF Error Comparison

| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |
| --- | --- | --- | --- |
|  | 2005 | 2006 | 2007 |
| January | 5.02 | 4.79 | 4.55 |
| February | 3.47 | 4.81 | 3.75 |
| March | 3.41 | 4.95 | 2.7 |
| April | 3.37 | 5.59 | 3 |
| May | 4.21 | 3.59 | 3.22 |
| June | 3.91 | 2.65 | 4.46 |
| July | 5.22 | 2.62 | 4.29 |
| August | 4.86 | 2.09 | 3.11 |
| September | 6.24 | 4.03 | 3.78 |
| Annual Average | 4.56 | 3.79 | 3.65 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 9/3 | 0:10 | 1:20 | Advisory | ARR less than 3000 MW. |
| 9/3 | 13:12 | 15:45 | Advisory | ARR less than 3000 MW. |
| 9/4 | 12:57 | 21:30 | Advisory | ARR less than 3000 MW. |
| 9/5 | 1:00 | 22:30 | Advisory | ARR less than 3000 MW. |
| 9/5 | 8:00 | 11:01 | Alert | ARR less than 2500 MW. |
| 9/5 | 16:56 | 20:15 | Alert | ARR less than 2500 MW. |
| 9/5 | 8:04 | 9:33 | EECP Step1 | EECP step 1. ARR less than 2300 MW. |
| 9/5 | 8:53 | 10:30 | OCN | Capacity shortage hours 15:00 to 19:00. |
| 9/6 | 11:18 | 21:40 | Advisory | ARR less than 3000 MW. |
| 9/6 | 4:00 | 4:45 | Alert | Capacity insufficiency HE 16:00 to 23:00. |
| 9/6 | 2:30 | 4:45 | OCN | Capacity shortage hours 16:00 to 23:00. |
| 9/6 | 11:40 | 13:00 | OCN | Capacity shortage hours 15:00 to 24:00. |
| 9/7 | 6:40 | 10:00 | Advisory | ARR less than 3000 MW. |
| 9/7 | 10:55 | 24:00 | Advisory | ARR less than 3000 MW. |
| 9/7 | 12:20 | 18:45 | Alert | ARR less than 2500 MW. |
| 9/8 | 0:15 | 3:00 | Advisory | ARR less than 3000 MW. |
| 9/8 | 9:15 | 24:00 | Advisory | ARR less than 3000 MW. |
| 9/8 | 12:30 | 20:40 | Alert | ARR less than 2500 MW. |
| Date | Start | End | Subject | Details |
| 9/9 | 0:15 | 2:30 | Advisory | ARR less than 3000 MW. |
| 9/9 | 9:35 | 23:30 | Advisory | ARR less than 3000 MW. |
| 9/9 | 7:00 | 16:33 | OCN | Capacity shortage hours 15:00 to 19:00. |
| 9/10 | 7:05 | 23:30 | Advisory | ARR less than 3000 MW. |
| 9/11 | 13:47 | 20:39 | Advisory | ARR less than 3000 MW. |
| 9/12 | 0:37 | 2:10 | Advisory | ARR less than 3000 MW. |
| 9/12 | 6:37 | 22:21 | Advisory | ARR less than 3000 MW. |
| 9/13 | 12:40 | 22:28 | Advisory | ARR less than 3000 MW. |
| 9/13 | 13:55 | 22:28 | Alert | ARR less than 2500 MW. |
| 9/14 | 5:56 | 17:45 | Advisory | ARR less than 3000 MW. |
| 9/15 | 11:59 | 19:24 | Advisory | ARR less than 3000 MW. |
| 9/16 | 13:50 | 19:07 | Advisory | ARR less than 3000 MW. |
| 9/16 | 15:31 | 19:07 | Alert | ARR less than 2500 MW. |
| 9/17 | 15:05 | 18:22 | Advisory | ARR less than 3000 MW. |
| 9/18 | 13:20 | 24:00 | Advisory | ARR less than 3000 MW. |
| 9/18 | 14:22 | 20:20 | Alert | ARR less than 2500 MW. |
| 9/19 | 0:15 | 3:00 | Advisory | ARR less than 3000 MW. |
| 9/19 | 6:30 | 23:45 | Advisory | ARR less than 3000 MW. |
| 9/19 | 16:20 | 20:15 | Alert | ARR less than 2500 MW. |
| 9/19 | 11:45 | 18:00 | OCN | Capacity shortage hours 15:00 to 18:00. |
| 9/21 | 15:23 | 18:05 | Advisory | ARR less than 3000 MW. |
| 9/22 | 12:17 | 19:00 | Advisory | ARR less than 3000 MW. |
| 9/23 | 17:05 | 19:12 | Advisory | ARR less than 3000 MW. |
| 9/24 | 16:20 | 18:20 | Advisory | ARR less than 3000 MW. |
| 9/26 | 15:14 | 18:35 | Advisory | ARR less than 3000 MW. |
| 9/26 | 16:09 | 18:35 | Alert | ARR less than 2500 MW. |
| 9/27 | 14:28 | 17:34 | Advisory | ARR less than 3000 MW. |
| 9/30 | 16:32 | 19:00 | Advisory | ARR less than 3000 MW. |

Transmission

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 9/13 | 13:00 | 14:45 | Alert | Loss of Kingsville-Alice loads Falfurrias Tr |
| 9/25 | 8:30 | 10:20 | Alert | Loss of Hondo-Moore loads Oaks-Poteet |
| 9/25 | 15:00 | 24:00 | Alert | Loss of San Miguel 138 kV-69kV loads Derby-Pearsall |
| 9/26 | 0:15 | 18:35 | Alert | Loss of San Miguel 138 kV-69kV loads Derby-Pearsall |

Other

9/5	Opened an adjustment Period replacement Reserve Market for hours 13:00 -19:00

9/6	Opened an adjustment Period replacement Reserve Market for hours 16:00 -24:00

9/6  15:06	Valley SPS armed and actuated as designed.

9/6  17:12	One 138 kV line and ten units tripped in the West Zone.

9/5 Laar Restoration