## Sheet1
Number | QSE | Document Section | Comment | Response
1 | Austin Energy | EIP V1.04 Section 3.3.8 | The xml structure of COP is such that it does not conform to the protocols Section 3.9.1 which states: "Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the Operating Day and the next seven Operating Days." Austin Energy firmly believes that this language implies unequivocally a single submission of a seven day COP. The current structure requires Market Participants to submit seven separate one-day COPs, requiring seven separate handshakes, seven encryptions, seven decryptions, seven validations, seven synchronous responses, and seven notifications. Austin Energy suggests allowing the first set of <starttime> and <stoptime> xml tags to span the seven day period specified in the protocols. | This is a point of apparent diagreement. There is no plan to change the interface at this point. It should be simply a matter of a software loop that iterates over each of the seven days. This also serves to keep message sizes smaller.
2 | Austin Energy | EIP V1.04 Section - general comment | Austin Energy continues to prefer using a single market interval ending designation (similar to the <tmPoint> tag), instead of a starttime stoptime pair, wherever applicable, to eliminate overlap issues, and to better represent the market interval as a defined time label, and not as an arbitrary elapsed time between arbitrary clock times. | This is a point of apparent disagreement. Changing this now would adversely impact the implementations of the other market participants.
3 | Austin Energy | EIP V1.04 Section 3.3.8 | Should unit ramp rates (up/down) be included in the COP, for better validation? | If the values were included in the message they still would not be used by the target system (MMS), so there is little point in sending them.
4 | Austin Energy | EIP V1.04 Section 3.3.8 | The EIP document should spell out the start hour for which the COP and other submissions cannot be updated for the operating day. | This is defned by protocols.
5 | Austin Energy | EIP V1.04 Section 3.3.4 | The value of <multihourblock> in the ASOffer structure should indicate a minimum number of hours, instead of a true/false value. | This would not be consistent with the capabilities of MMS.
6 | Austin Energy | EIP V1.04 Sections 4 and 5 | The ERCOT wind forecast query or notification are not specified in the EIP document. Protocols section 4.2.2 states: "Each hour, ERCOT shall provide, through the Messaging System, the WGRPP forecasts for each WGR to the QSE that represents that WGR and shall post each WGRPP forecast on the MIS Certified Area." | We will look at the possibility of adding this capability in the next version of the spec.
7 | Structure Group | 3.3.5 & 4.3.19 | Both the AS Trade and the AS System plan use the ASSchedule container/element. In the AS Trade, asType is shown outside of ASSchedule, but in the AS System plan, asType is shown inside the ASSchedule container. Which one is correct? | Both are correct. Part of an AS trade is a schedule of ancillary services. An AS system plan provides schedules of ancillary services. This is just a matter of reusing components.
8 | Structure Group | 3.3.10 & 3.3.11 | In the DAM Energy Only Offer and DAM Energy Bid, the BidID is identified as a key field. We are trying to get clarification on how ERCOT systems will use this ID. Since the document indicates that this offer and bid information will be updated, queried and canceled based on this ID, then is it possible to have more than one offer or bid for the same interval as long as the BidIDs are different? | Yes, it is possible to have more than one offer or bid for the same interval, provided that the bidIds are different.
9 | Structure Group | 5.3.1 | For Notices and Alerts, figure 112 describes several different notification types that do not have a separate container described for the data they deliver. Where does this data show up in the notification structure depicted in figure 111. Is it in the Details tag? Also, since there a different number of data elements for each notice, how does the data appear? Does it appear i tags represented by the names of the data elements, or is it all concatenated in the Details tag? | The container used for these is the Notification structure shown in figure 111.
10 | Structure Group | Appendix I | Issue ID 55 states, "Need to update error messages in section 3.4 to reflect implementation". Does this mean that the interval associated with the error will no longer be identified in a separate 'Interval' tag? | No. It just means that we will update the document to reflect specific error codes where possible.
| Centerpoint | General | In Section 5, entitled "Notifications", of the subject document, it is stated, "Each Market Participant using the external interface would be required to provide a listener interface for the receipt of notification messages, compliant with the interface provided by ERCOT." It is our understanding that ERCOT will relay the notifications to each Market Participant (MP) via the public Internet using HTTPS protocol. However, we would prefer that ERCOT send its notifications and alerts to us via private WAN, and only send them via the Internet to those Market Participants who do not have WAN. The following details our reasoning in this regard. 1. CenterPoint Energy’s Control Center and Corporate security policies prohibit inbound access from the internet to critical servers. The web services server is at our control center and hence subject to critical infrastructure security policy. 2. As you know all our current access to ERCOT (inbound/outbound) from the Energy Control center is via the ERCOT WAN. System dispatcher only access ERCOT web portal via the internet as a secondary path or when outside the control center perimeter. 3. There is no direct internet access into our control center. Our internal processes expect Control Center systems to remain functional even when the corporate internet infrastructure is unavailable for various reasons (maintenance, cyber attacks, other…) 4. We have encouraged our developers to rely more on web services in obtaining market notifications, rather than “web scrapping” CNP plans to use web service to facilitate exchange of sensitive operational information with ERCOT (outages, outage status notifications, NOMCR, NOMCR status notifications, market notifications.) Our preference is that both inbound and outbound exchanges with ERCOT go through the established WAN, and only use the internet as a secondary path for only outbound traffic. The current objection that web services may interfere with ICCP data traffic will need to be substantiated with test data. | The use of the internet is the current direction of ERCOT.
| Reliant | General | My only comment on the v1.04 xml spec is I liked having the hour on the mRID (Generated mRID values will not have hours). It would be nice to see the mRID in submit responses, bid set accepted notifications, etc. I currently use the messageid to tie submits and notifications together, and put the hour ending in the externalId. I get the externalId back in my notifications so I can reconstruct the mRID, but not in submit responses. | The hour can be appended to the mRID to identify a specific hour. Where the get mRID interface generates the main part of the mRID, you can append with .<hour> as described in section 2.3.4.
| Luminant | 2.1.1 | Will this be the UserID or the CertID? | UserID
| Luminant | 2.3.2 | ERCOT should never round times submitted. Rather, this should fail validation and an error returned to the QSE. | What we are trying to do is force a validation error that would return a meaningful error message. Unfortunately, we would need to 'bail out' on the first error if we don't round.
| Luminant | 2.3.3 | This maintains the interpretation that mRID remains in the payload tags and ExternalID is supported in Creates, Updates and Cancels.. | The mRID is the key required for updates and cancels.
| Luminant | 3.3 | For cancellations, this maintains the interpretation that mRID remains in the payload tags. | The mRID is the key that would need to be supplied within the payload for cancels.
| Luminant | 3.3 | Again, the interpretation here is: Bids to cancel are identified in the BidSet using the mRID in the BidSet, not the RequestPackage. Specific bids (plural) to cancel can be identified in the BidSet so long as they are of common type. Since the XSD shows cardinality for multiple common types within the BidSet, it stands-to-reason that this is where the mRIDs are identified not in the RequestPackage’s <ID> tag. | No use the ID in the Request package. More than one ID can be specified.
| Luminant | 3.3 (ref to figure 16) | Implies the payload of the bid need not be submitted, fine. But the information to “uniquely identify the bid/offer/trade/schedule” is the mRID and that does reside within the payload as per figure 16, Bid Class, below. | Need to remove this sentence, as it is incorrect.
| Luminant | 3.3 | Implies all types of submissions. | Yes, the externalID is allowed for all types of submissions.
| Luminant | 3.3.4 | ASCurveData and ASData do not seem to be represented in the diagram but are in the XML examples. Is the diagram up-to-date? | The diagram and XSD are correct, but the text, figure 28 and example need to be revised to use the tags OnLineReserves, RegDown and OffLineNonSpin
| Luminant | 3.3.14 | There is no crrAccountHolderId associated with this transaction. The protocols are in error and should probably be fixed. This should be optional and NOT a key field. PTP Obligations are bid on and bought in the DAM by QSEs and settled in the Real-time based on those real-time prices.. There is no data exchanged with the CRR system for these PTP Obligations. | For PTP obligation, there is no CRR account holder presently. That is why we showed it as optional rather than a required field ( please see the dashed line on this box to signify that it is optional). We provided this filed as a place holder in case any changes in future
| Luminant | 3.5.2, figure 61 | Why is this not part of the payload? How are multiple mRIDssubmitted? | A list of mRID values can be sent using a list of ID values within the request package of the message. This provides a much simpler interface as there is no need for the requester to encode a BidSet.
| Luminant | 3.5.4 | mRID should be in the payload not here. How are multiple mRIDs supplied? How can ExternalID be used? | Using ID vaklues in the Request package is correct. The externalID can not be used for get requests, as it is not maintained by MMS and not persisted by the integration layer.
| Luminant | 3.5.4 | This is counter to the rule that only like types may be canceled at a time. | Example will be corrected.
| Luminant | 4 | Will market queries be a synchronous or asynchronous response? | The current direction is to make the response synchronous.
| Luminant | 4.3 | Do you know the estimated date these will be defined and updated in this document? THIS IS CRITICAL! | Absolutely agree that this is critical. The best guess is now November, after the next delivery of MMS in late October. This also impacts section 5.
| Luminant | 4.3.10 | Why doesn’t DynamicRatings have time component? Also, what is equipment? What’s the relationship of equipment and Resource? Equipment and electrical bus? | Need to add a time component, but need to discuss the best/most useful way of doing this, such as providing the time on the request. Any relationships between equipment and resources or equipment and buses would be known through the network model.
| Luminant | 4.3.11 | Same. Why no time component with the information? | Need to add a time component, but need to discuss the best/most useful way of doing this, such as providing the time on the request.
| Luminant | 4.3.15 | No time component? | Need to add a time component, but need to discuss the best/most useful way of doing this, such as providing the time on the request.
| Luminant | 4.3.16 | Should ShiftFactor have time dimension? | Need to add a time component, but need to discuss the best/most useful way of doing this, such as providing the time on the request.
| Luminant | 4.3.16 | Looks like equipment is a transmission branch. | Yes
| Luminant | 4.3.21 | Can we get an example of what this data will look like? | We will try to provide examples when we get them from the source system.
| Luminant | 4.3.21 | What’s in these 2 fields? MWs? Or just true or false? This XML structure is the same as the one of StartupShutdown notification. | True or false.
| Luminant | 5.3.1 | We are required to provide a synchronous response to all messages from ERCOT. Does this imply that an addition or separate acknowledgement is required? If so, will the acknowledgement for alerts be asynchronous? | The acknowledgement for alerts is a separate interface as described in section 6. The Acknowledgement for Notifications is different, and is used to verify that you received each and every Noitification so that ERCOT can either retry or send the next one.
| Luminant | 5.3.2 | Does not jive with rule for common product types listed in issue 56 of this document. | Example will be corrected. Exanmple in 5.3.3 also corrected.
| Luminant | 5.3.4 | Will a Get PendingTrades request also be supported? | Not currently planned. This would seem to be the same as a get for unconfirmed trades.
| Luminant | 5.3.4 | How are trades that are partially confirmed handled? If I report a trade from 10:00 through 18:00 but my counterparty reports a trade from 11:00 through 19:00, are there any hours that are confirmed? If I submit the trade separately for each hour, but my counterparty submits it as a span of hors, does it effect how the confirmations are done? | The confirmation ( matching of the trades) are done on hourly basis. In the example, hour 11 to 18 shall be confirmed. As far as confirmation of the trades are concerned, it does not matter wether one party submits it for individual hour and the other one for the range of the hours.
| Luminant | 5.3.5 | when would an LMP be supplied? It seems only SPP’s from the DAM would be available. OR Does this imply that we get one of these XML messages every time SCED runs? | The section refers to the energy offer award. We provided these two fileds as optional fileds at the time that it was not quite clear whether or not the SPP/LMPs are provided as part of the awards. The assumption was that, if MMS provides such information as part of energy awards, we will have a place holder for it. The LMPs and SPPs are actually coming from a different XML payload , section 4.3.5. Section 5.3.5 indicates the energy award for the DAM only.
| Luminant | 5.3.8 | What is this? | This section refers to the AS awards. The self schedule MW field was provided as an optional field which was supposed to show how much ancillary service a resources is self providing ( in addition to what was awarded in the market). This information may not be available at the time that Ancillary service market is cleared and as such, it may not be required and populated any more.
| Luminant | 5.3.13 | The Startup instructions MUST also contain the Startup Price and MinEnergy Price from the clearing in both DAM and RUC cases. This data is required by ERCOT settlements, must be passed to settlements, and therefore needs to be passed to MPs for shadow settlements. Those values are not always based on an offer supplied by the MP. | It is up to MMS team and MMS vendor to provide such functionality. If they provide such functionality, we could easily accommodate it in our XML schema.
| Luminant | General | When will the XML Non-Spin deployments be added to this document and sandbox? I believe this was decided in TPTF to be XML via API interface. | Once, MMS finalizes the design of such functionality, we will add its XML schema
| Luminant | General | When will the Wind Generation Resource Production Potential (WGRPP) notification be added to this document & sandbox? | Awaiting finalization of the design
| Luminant | General | Can some examples regarding multiple cancels of the same resource for multiple hours within the same trade date be added to this document? | Yes.
| Luminant | General | For submissions where the resource is a required field in the MRID, will the combined cycle ID field be part of the MRID key? Can we have an example how this will look? | No, the combined cycle is currently not part of the mRID. The use of combinedCycle is an open issue with ABB.
| Luminant | General | Can we provide an External ID field for cancellation messages? For cacellations we do not receive a MRID with an hour field attached to the response from ERCOT. If some cancellations were accepted and some were not accecpted, we have no way of determining which hours were cancelled. | ExternalId is not used for get or cancel. You can append the hour to the mRID to cancel a specific hour (as described in section 2.3.4)
| Luminant | General | Is the ‘Create’ and ‘Update’ verb synonymous with submissions? For instance if I submit the first COP for a trade date, can I use the ‘Update’ verb if no record exists in the MMS for that resource? | For the interfaces in section 3, they are synonymous. Use 'create' in both cases.