## Slide 1: Texas Regional Entity Report
November 2007

## Slide 2: Performance Highlights
ERCOT’s Control Performance Standard (NERC CPS1) score for September – 128.83
Initial scores for September indicate all non-wind-only QSEs passed the PRR 525 measure
  This is the third straight month all non-wind-only QSEs have passed this measure
Overall control performance score using the PRR 525 measure (SCPS) for non-wind-only QSEs > 95%

## Slide 3: LaaR Deployment History

## Slide 4: Texas RE Monthly Summary
For September……….
  Protocol & Operating Guides violations
    0 new alleged
  NERC Standards violations
    1 new alleged
  3 new events reported
    2 Compliance Reviews in progress
  Final on-site Compliance Audit completed for 2007
  2 registration appeals denied by NERC Board of Trustees Compliance Committee
  2 pending registration appeals

## Slide 5: NERC Standards Compliance
Critical Infrastructure Protection (CIP) – Applies to all Entities listed in the NERC Compliance Registry in accordance with Implementation Plan for CIP Standards.
Protection and Control (PRC) – One or more PRC Standards apply to most Entities listed in the NERC Compliance Registry.
FAC-003: Transmission Vegetation Management Program – Prevent and report vegetation-related outages. Applies to all Transmission Owners with transmission lines that operate at 200 kV and above. Zero tolerance policy.

## Slide 6: 2008 Annual ERCOT Operations Training Seminar
Planning of the 2008 seminar – cooperative effort between the Seminar Working Group and Nodal Training Team.
Seminar will meet many training needs:
  Focus to be on Nodal Basic Training (Basic Training Program)
  NERC Training Requirements – PER-002 (Mandatory requirement for BA & TOP Operators – 5 days)
  ERCOT Operating Guide Requirements – Section 1.8.2 ( 40 hours of System Emergency Training for ERCOT ISO, ERCOT Transmission, and QSE Operators)
  NERC Continuous Education Hours (CEH’s) for RC, BA, TOP, & IA Operators.

## Slide 7: 2008 Annual ERCOT Operations Training Seminar
Priority given to target group of Operators – ERCOT ISO, TDSP, & QSE
Six (6) sessions – March 24th through May 2nd
Course length – 4 ½ days; Mondays, 9:00 am through Fridays, noon
Location – Austin Met Center
Registration fee still being reviewed - <$200, possibly considerably less
Registration will be through ERCOT’s Learning Management System
Attendees are responsible for making their own hotel reservations

## Slide 8: Texas RE Delegation Agreement
Amended and Restated Regional Delegation Agreement (RDA) between Texas RE and NERC as approved by the Texas RE Board sent to NERC on October 2nd
NERC Staff seeking an extension for the FERC Filing of the RDAs
  FERC Filing was to be made on October 16th
  Allows the NERC Board of Trustees more time to review the 8 RDAs
  NERC Board of Trustees to approve on October 23rd
NERC will file NERC Board of Trustees approved RDAs at FERC

## Slide 9: Texas RE Fall Workshop
Planned for November 2nd – Austin Met Center
Update participants on the 2007 Compliance Monitoring & Enforcement Program – provide a “sneak peek” at the 2008 Compliance Program
Proposed topics
  Texas RE Organization and Entity roles
    NERC Compliance Monitoring & Enforcement Program
    ERCOT Protocol and Operating Guides compliance
  Organization Registration
  Standards overview
  Assessing compliance
  Enforcement and sanctions
  Q & A
Speakers to include Texas RE and NERC Staff

## Slide 10: Texas Regional Entity
Report Details

## Slide 11: NERC CPS1 Performance
ERCOT’s CPS1 Performance
  September Performance
    September performance comparison
      September 2007: 128.83
      September 2006: 142.51
    12 month rolling average comparison
      October 2006 September 2007: 131.47
      October 2005 September 2006: 141.50
PRR 525 Performance
  Scores for September indicate all 34 non-wind-only QSEs passed the measure
  Scores posted on the ERCOT Compliance Website
    SCE Performance Scores

## Slide 12: ERCOT CPS1 Performance Comparison

## Slide 13: ERCOT CPS1 Scores

## Slide 14: ERCOT’s CPS1 Monthly Performance

## Slide 15: ERCOT CPS1 by Interval

## Slide 16: QSE PRR 525 10-Minute Interval Scoring

## Slide 17: PRR 525 Passing 10-Min Interval Percentage Trends

## Slide 18: September 2007 Resource Plan Performance Metrics

## Slide 19: September 5th NERC DCS Event
Loss of transmission facilities caused by weather
1,084 MW of generation lost
Frequency dipped to 59.739 Hz
Load acting as a Resource (LaaR) manually deployed
EECP Step 1 declared due to low reserves
NERC reportable disturbance
Frequency recovered in 6 minutes – No violation of NERC BAL-002-0
>1,150 MW LaaR deployed across ERCOT Region within 10 minutes
  One QSE with LaaR did not meet 10-minute requirement
  First time deployment for that LaaR (3 MW Obligation)
Event Investigation and Compliance Review underway

## Slide 20: LaaR Deployment – September 5th
Significant Improvement in LaaR Deployment Performance on September 5th
Exceeded 1,150 MW Obligation
  1,169 MW Deployed Within 10-Minutes
PRR 714 effective August 1st requires…
  LaaR qualification testing – actual load interruption
  Additional periodic LaaR testing at least once in every 365 days
  Disqualification for 2 failures within any rolling one-year period
  If disqualified, LaaR can reapply after 6 months

## Slide 21: Organization Registration Status
Of 227 entities registered in the ERCOT Region, 8 entities officially appealed their registration
  4 appeals resolved by the Texas RE
  2 Registered Entity appeals heard by NERC Board of Trustees Compliance Committee (BOT CC) – both appeals denied
    1 entity appealed their registration as a Transmission Owner
    1 entity appealed their registration as a Transmission Owner/Planner
  2 appeals pending and will go before the BOT CC for resolution
    2 entities appealing their registration as a Generator Operator

## Slide 22: 2007 Compliance Audits

## Slide 23: NERC Functional Entity Types
DP – Distribution Provider
GO – Generator Owner
GOP – Generator Operator
TO – Transmission Owner
TP – Transmission Planner
RC – Reliability Coordinator
BA – Balancing Authority
TOP – Transmission Operator
PA – Planning Authority
TSP – Transmission Service Provider
RP – Resource Planner
PSE – Purchasing-Selling Entity

## Slide 24: Compliance Reviews Events by Month

## Slide 25: Violations of ERCOT Protocols Reported by Month

## Slide 26: Violations of NERC Standards Reported by Month

## Slide 27: NERC Reliability Standard Violations Post June 18th
July – Alleged violations of PRC-008 R1 & R2 discovered during audit
  Implementation and Documentation of Under Frequency Load Shedding (UFLS) Equipment Maintenance Program
  Documentation of the maintenance and testing program was not provided
  Violation Severity: Level 4 (Severe)
  Violation Risk Factor: Medium
  Potential Impact: Low (incomplete documentation of work performed)
    Less than 1% of total UFLS in ERCOT
  Category – Administrative

## Slide 28: NERC Reliability Standard Violations Post June 18th
September – Alleged violation of PRC-005 R2 discovered through Self-Certification
  Transmission and Generation Protection System Maintenance and Testing
  Maintenance & Testing did not occur within the identified intervals
  Violation Severity: Level 2 (Moderate)
  Violation Risk Factor: Lower
  Potential Impact: Low (small non-345 KV system; limited number of devices late on maintenance)
  Category – Technical

## Slide 29: NERC Standards Self-Reported Violations Pre-June 18th

## Slide 30: Risk Factors for Self-Reported Violations Pre-June 18th

## Slide 31: Self-Reported Violation Categorization