ERCOT Operations Report

October 2007 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration |  |
| --- | --- | --- | --- |
| 10/2 17:32 | 59.865 | 1 m 55 s | 615 MW Unit trip |
| 10/9 17:51 | 59.863 | 1 m 24 s | 620 MW Unit trip |
| 10/10 7:32 | 59.898 | 2 s | 385 MW Unit trip |
| 10/12 20:46 | 59.809 | 1 m 44 s | 630 MW Unit trip |
| 10/15 0:06 | 60.111 | 38 s | 500 MW SCE during 2225 schedule change. |
| 10/16 5:50 | 60.107 | 30 s | 4,200 MW schedule change across 06:00 |
| 10/16 6:44 | 60.107 | 16 s | Held Interval |
| 10/21 3:02 | 60.104 | 4 s | 285 MW SCE. |
| 10/22 21:00 | 60.109 | 56 s | 820 MW SCE swing over previous 10 minutes. |
| 10/23 19:24 | 59.844 | 1 m 16 s | 635 MW Unit trip |
| 10/29 5:25 | 59.893 | 20 s | Positive SCE corrected over IE 06:00. RRS deployed 05:01 - 05:41. |
| 10/29 9:50 | 59.828 | 1 m 6 s | 595 MW Unit trip |
| 10/30 15:30 | 59.892 | 2 s | 2 Unit train totaling 310 MW tripped |
| 10/30 21:43 | 59.895 | 24 s | 3 Unit train totaling 450 MW tripped while ramping down |
| 10/31 22:02 | 59.882 | 56 s | 1500 MW SCE swing over ten minute ramp |
| 10/31 23:00 | 60.102 | 12 s | 600 MW SCE |

Deployed Responsive (Reported Above)

| ID | Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- | --- |
| 1 | 10/2 17:32:08 | 10/2 17:53:10 | 0:21:02 | 534 |  |
| 2 | 10/3 0:02:24 | 10/3 0:16:08 | 0:13:44 | 331 | SCE |
| 3 | 10/3 15:37:36 | 10/3 15:47:20 | 0:09:44 | 321 | Unit Trip |
| 4 | 10/9 17:51:44 | 10/9 18:08:40 | 0:16:56 | 544 |  |
| 5 | 10/10 7:32:44 | 10/10 7:40:48 | 0:08:04 | 366 |  |
| 6 | 10/10 10:17:40 | 10/10 10:44:14 | 0:26:34 | 326 | Control issues during fail over |
| 7 | 10/12 12:04:28 | 10/12 12:29:16 | 0:24:48 | 336 | SCE |
| 8 | 10/12 19:03:38 | 10/12 19:14:36 | 0:10:58 | 326 | SCE |
| 9 | 10/12 20:46:42 | 10/12 21:26:14 | 0:39:32 | 819 |  |
| 10 | 10/12 22:02:26 | 10/12 22:17:10 | 0:14:44 | 336 | Depleted Up Reg due to low SCE over previous hour. Multiple Cat 2 & 3 deployments to Reg providers |
| 11 | 10/14 10:01:56 | 10/14 10:24:38 | 0:22:42 | 310 | SCE |
| 12 | 10/14 22:59:32 | 10/14 23:27:44 | 0:28:12 | 321 | SCE |
| 13 | 10/17 22:50:03 | 10/17 22:59:20 | 0:09:17 | 326 | SCE |
| 14 | 10/21 15:19:46 | 10/21 15:47:38 | 0:27:52 | 321 | SCE. NSRS deployed at 15:15 |
| 15 | 10/22 17:06:22 | 10/22 17:35:54 | 0:29:32 | 310 | Communication failure with QSE (RTU) 17:00 - 17:25 |
| 16 | 10/23 19:24:07 | 10/23 19:45:01 | 0:20:54 | 875 |  |
| 17 | 10/25 15:00:32 | 10/25 15:14:50 | 0:14:18 | 315 | Held interval. Control issues during fail over |
| 18 | 10/27 22:57:26 | 10/27 23:06:38 | 0:09:12 | 346 | SCE |
| 19 | 10/29 5:01:36 | 10/29 5:41:16 | 0:39:40 | 392 | SCE |
| 20 | 10/29 6:02:56 | 10/29 6:23:18 | 0:20:22 | 310 | Unit Trip |
| 21 | 10/29 9:50:28 | 10/29 10:14:38 | 0:24:10 | 723 |  |
| 22 | 10/30 15:31:02 | 10/30 15:41:06 | 0:10:04 | 397 |  |
| 23 | 10/30 21:43:42 | 10/30 21:54:50 | 0:11:08 | 382 |  |
| 24 | 10/31 6:10:14 | 10/31 6:19:34 | 0:09:20 | 321 | SCE |
| 25 | 10/31 22:02:50 | 10/31 22:21:32 | 0:18:42 | 448 |  |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 30 | 13 | 2 | 45 |
| Bryan Area | 0 | 0 | 1 | 0 | 1 |
| Corpus | 0 | 0 | 0 | 0 | 0 |
| DFW | 0 | 12 | 0 | 4 | 16 |
| E RIO | 0 | 3 | 7 | 0 | 10 |
| Houston | 0 | 11 | 25 | 8 | 44 |
| Laredo | 71 | 0 | 0 | 0 | 71 |
| North | 0 | 4 | 13 | 9 | 26 |
| Northeast | 0 | 0 | 0 | 1 | 1 |
| San Antonio | 0 | 0 | 7 | 11 | 18 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 14 | 1 | 0 | 15 |
| Western | 0 | 6 | 1 | 10 | 17 |
|  | 71 | 80 | 68 | 45 | 264 |

| Historical Totals | Oct-06 | Sep-07 | Oct-07 |
| --- | --- | --- | --- |
| Austin | 3 | 31 | 45 |
| Bryan Area | 8 | 0 | 1 |
| Corpus | 20 | 7 | 0 |
| DFW | 16 | 21 | 16 |
| E RIO | 10 | 2 | 10 |
| Houston | 0 | 15 | 44 |
| Laredo | 80 | 90 | 71 |
| North | 2 | 54 | 26 |
| Northeast | 13 | 0 | 1 |
| San Antonio | 0 | 11 | 18 |
| South | 0 | 3 | 0 |
| W RIO | 97 | 0 | 15 |
| Western | 6 | 1 | 17 |
| Total | 255 | 235 | 264 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple - Tradinghouse & Temple Switch - Lake Creek 345 kV | Temple Pecan Creek - Lake Creek 138 kV | 22 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Elkton - Athens | 9 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Nacodoches SE Auto #1 | 7 |
| Marion - Zorn & Clear Springs 345 kV | Seguin - Seguin West 138 kV | 6 |
| Midland - Odessa EHV Switch 345 kV | Moss Switch - Odessa Southwest 138 kV | 6 |
| Fisher Road - Oklaunion & Bowman | Long Creek - Graham 345 kV | 5 |
| Monticello - Farmersville 345 kV | Monticello - Sulfur Springs Switch 345 kV | 5 |
| Paris Switch - Valley SES & Valley South | Valley SES - Brookstone Tap 138 kV | 5 |
| Big Brown SES - Jewett 345 kV | Big Brown SES - Jewett 345 kV | 4 |
| Temple Pecan Creek - Tradinghouse - Temple Switch 345 kV | Goldthwaite 138/69 kV auto | 4 |
| Snyder - Sun Switch 138 kV | Ennis Creek Switch 138/69 kV | 4 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Shamburger Switch Auto #1 | 4 |
| Oklaunion - Bowman 345 kV | Lake Pauline 138/69 kV auto 1 | 4 |
| Bowman Switch - Graham 345/138 kV T1 | Wichita Falls -Rathgeber 138 kV | 3 |
| Temple Pecan Creek - Tradinghouse - Temple Switch 345 kV | Waco West - Lorena 69 kV | 3 |
| North Edinburg - Rio Hondo 345 kV | South McAllen - Las Milpas 138 kV | 3 |
| Twin Buttes - San Angelo 345KV | San Angelo Red Creek 345/138KV Auto #2 | 3 |
| Fisher Road - Oklaunion & Bowman | Lake Pauline - Liberty REA 69 kV | 3 |
| West - North Stability Limit |  | 3 |
| Temple Pecan Creek - Tradinghouse - Temple Switch 345 kV | Watson Chapel - Robertson 138 kV | 2 |
| Temple Pecan Creek - Tradinghouse - Temple Switch 345 kV | Waco West - Waco Woodway 138 kV | 2 |
| Tricorner - Martin Lake & Forney Switch - Elkton 345 kV | Elkton - Athens Tap 138 kV | 2 |
| Big Brown - Venus Switch 345 kV | Big Brown - Jewett 345 kV | 2 |
| Morgan Creek 345/138 kV auto 2 | Morgan Creek 345/138 kV auto 1 | 2 |
| Morgan Creek 345/138 kV auto 1 | Midland East - Big Spring 138 kV | 2 |
| Sonora 138/69 kV auto | Friend Ranch - Ozona 69 kV | 2 |
| Lon Hill - Nelson Sharpe 345 kV | Barney Davis - Alazan 138 kV | 2 |
| Lon Hill - Nelson Sharpe 345 kV | Barney Davis - Nelson Sharpe | 2 |
| Bowman Switch - Graham 345/138 kV T1 | Wichita Falls S Switch - Arrowhead Meter | 1 |
| Graham - Sweetwater Cogen & Graham - Long Creek 345 kV | Abilene South - Potosi Tap 138 kV | 1 |
| Holt Switch - Andrews North 138 kV | Holt Switch - Emma Tap 69 kV | 1 |
| Mc Donald - Morgan Creek 138 kV | Sprayberry Switch - Colorado River Municipal Water District 138 kV | 1 |
| Menard - Gillespie 138 kV | Menard - Hext 69 kV | 1 |
| Morgan Creek 345/138 kV auto 1 | Morgan Creek 345/138 kV auto 2 | 1 |
| Moss Switch 345/138 kV T1 | Moss Switch - Odessa Southwest 138 kV | 1 |
| Nelson Sharpe - Rio Hondo 345 kV | Celanese Bishop - Nelson Sharpe 138 kV | 1 |
| Paris Switch - Valley SES & Valley South | Paris Switch 345/138 kV Auto | 1 |
| Sandow - Temple 345 kV | Killeen Fort Hood West - Killeen Clark Road | 1 |
| Sandow Switch - Sandow SES 138 kV | Sandow 345/138 kV Auto #1 | 1 |
| STP - Dow 345 kV | STP - Hillje 345 kV | 1 |
| Watermill - Tricorner & Trinidad SES 345 kV | Big Brown SES - Jewett 345 kV | 1 |
| West Denton 345/138 kV Auto #1 | Collin SES - Frisco 138 kV | 1 |
| West Columbia Main - Sweeny Cogen | Sweeny Cogen - Old Ocean 69 kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North - Houston | 7 |
| West - North | 6 |
| South - Houston | 5 |
| North - West | 2 |

New RAP

10/1	STP- DOW 345 kV double circuit.

10/15	Goldthwaite Auto PCAP.

New Procedures/Forms/Operations Bulletins

10/20	POB 350 - Frequency Control Desk

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

10/12 	Held 08:45 Interval.  Exporter application issues.

10/16 	Held 06:45 Interval.   Incorrect Hour – Ahead generation values.

10/17   Extended Day Ahead Ancillary Service Market.  Portal issues.

10/19 	Held 08:45 Interval.  Oracle issues.

10/21	Held 09:00 Interval.  Oracle issues.

10/22 	Held 08:45 Interval.  Oracle issues.

10/23	Held 08:45 Interval.  Oracle issues.

10/25 	Held 14:45 Interval.  Application failed to start during fail over.

10/28   Extended Day Ahead Ancillary Service Market. Requirements were published late.

10/29   Held 15:00 Interval.  Error in script migrated in October release.

## ERCOT peak (Unofficial)

10/1	17:00   53,975

Yearly MTLF Error Comparison

| MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
| --- | --- | --- | --- |
| Month |  |  |  |
|  | 2006 | 2007 |  |
| January | 4.79 | 4.55 |  |
| February | 4.81 | 3.75 |  |
| March | 4.95 | 2.7 |  |
| April | 5.59 | 3 |  |
| May | 3.59 | 3.22 |  |
| June | 2.65 | 4.46 |  |
| July | 2.62 | 4.29 |  |
| August | 2.09 | 3.11 |  |
| September | 4.03 | 3.78 |  |
| October | 3.63 | 3.08 |  |
| Annual Average | 3.79 | 3.59 |  |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End |  | Event |
| --- | --- | --- | --- | --- |
| 10/2 | 16:17 | 18:10 | Advisory | ARR below 3000 MW. |
| 10/5 | 12:15 | 18:15 | Advisory | ARR below 3000 MW. |
| 10/7 | 15:00 | 20:50 | Advisory | ARR below 3000 MW. |
| 10/8 | 14:03 | 17:10 | Advisory | ARR below 3000 MW. |
| 10/9 | 14:14 | 18:25 | Advisory | ARR below 3000 MW. |
| 10/10 | 16:20 | 18:05 | Advisory | ARR below 3000 MW. |
| 10/12 | 14:35 | 18:15 | Advisory | ARR below 3000 MW. |
| 10/13 | 15:05 | 18:33 | Advisory | ARR below 3000 MW. |
| 10/14 | 13:45 | 24:00 | Advisory | ARR below 3000 MW. |
| 10/14 | 15:25 | 21:45 | Alert | ARR below 2500 MW. |
| 10/15 | 0:15 | 6:10 | Advisory | ARR below 3000 MW. |
| 10/15 | 6:33 | 9:18 | Advisory | ARR below 3000 MW. |
| 10/15 | 13:41 | 17:46 | Advisory | ARR below 3000 MW. |
| 10/17 | 4:56 | 9:09 | Advisory | ARR below 3000 MW. |
| 10/17 | 14:58 | 20:00 | Advisory | ARR below 3000 MW. |
| 10/19 | 0:09 | 3:04 | Advisory | ARR below 3000 MW. |
| 10/19 | 14:42 | 18:25 | Advisory | ARR below 3000 MW. |
| 10/20 | 15:57 | 18:45 | Advisory | ARR below 3000 MW. |
| 10/20 | 23:18 | 24:00 | Advisory | ARR below 3000 MW. |
| 10/21 | 0:00 | 1:40 | Advisory | ARR below 3000 MW. |
| 10/21 | 12:48 | 21:32 | Advisory | ARR below 3000 MW. |
| 10/21 | 14:23 | 20:00 | Alert | ARR below 2500 MW. |
| 10/21 | 23:16 | 24:00 | Advisory | ARR below 3000 MW. |
| 10/22 | 0:00 | 3:20 | Advisory | ARR below 3000 MW. |
| 10/22 | 5:40 | 10:10 | Advisory | ARR below 3000 MW. |
| 10/23 | 6:58 | 10:32 | Advisory | ARR below 3000 MW. |
| 10/23 | 22:11 | 0:00 | Advisory | ARR below 3000 MW. |
| 10/24 | 0:00 | 0:30 | Advisory | ARR below 3000 MW. |
| 10/24 | 6:47 | 17:30 | Advisory | ARR below 3000 MW. |
| 10/24 | 19:22 | 22:30 | Advisory | ARR below 3000 MW. |
| 10/26 | 5:26 | 7:50 | Advisory | ARR below 3000 MW. |
| 10/26 | 16:28 | 20:02 | Advisory | ARR below 3000 MW. |
| 10/27 | 8:16 | 21:02 | Advisory | ARR below 3000 MW. |
| 10/28 | 15:46 | 21:48 | Advisory | ARR below 3000 MW. |
| 10/28 | 19:33 | 21:48 | Alert | ARR below 2500 MW. |
| 10/29 | 9:54 | 20:21 | Advisory | ARR below 3000 MW. |
| 10/30 | 19:08 | 21:00 | Advisory | ARR below 3000 MW. |
| 10/31 | 22:00 | 23:59 | Advisory | ARR below 3000 MW. |

Transmission

10/1 10:00 – 18:00 Transmission Alert.  Loss of South Channel - Shell creates an island/voltage collapse condition in the area.

10/29 12:30 – 18:00 Transmission Alert.  Loss of Menard Auto loads Gillespie - Phillips Mason Tap

Other

10/4 09:50	Simultaneous loss of four 345 kV lines at a bus in East Texas.