Tentative

- Generator shall tune unit in local area mode using equivalent short circuit impedance. Generally 1 to 3 Hz.

  - Phase compensation

  - Field set Gain

- Generator shall field tune the PSS

- Have DWG review that every 5 years to help with inter-area oscillations.

- DWG may specify changes to settings.

- Should we consider an exemption criterion? (Induction machines?. MW size)

- Should we address retrofitted machines with new excitation systems.

Existing machines with PSS turned off which were developed before 2001 (old technology)

- ERCOT planning should examine settings and then order them to turn them on or off.  If directed to turn them off ERCOT shall provide an exemption.

Existing machines with PSS turned off which were developed after 2001 (New technology)

- Same as new generators.