| OGRR Number | 206 | OGRR Title | Black Start Satellite Phones |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | November 13, 2007 |  |  |
| Operating Guide Section Requiring Revision |  | 4.6.5, Emergency Back Up Communication Facilities Criteria |  |  |
| Proposed Effective Date |  | ## To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) will require Transmission Service Providers (TSPs) that have contracted Black Start resources or designated Black Start transmission corridors located within their transmission system to have a satellite phone as a backup communication system that is compatible with ERCOT’s satellite phone. |  |  |
| ###### Overall Market Benefit |  | This OGRR ensures that ERCOT and TSPs are able to communicate in Black Start conditions when alternative methods of communication may not be available and thus may improve reliability. |  |  |
| ###### Overall Market Impact |  | None. |  |  |
| ###### Consumer Impact |  | None. |  |  |
| ###### Procedural History |  | - On 10/18/07, this OGRR was posted. - On 11/12/07, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 11/13/07, the Operations Working Group (OWG) considered this OGRR. |  |  |
| ###### OWG Decision |  | On 11/13/07, the OWG was in consensus to recommend approval of this OGRR as modified by the 11/12/07 OGRTF comments. |  |  |
| ###### Summary of OWG Discussion |  | On 11/13/07, the OWG reviewed the OGRTF comments. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Improved reliability and operations |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 | Operational readiness for potential Black Start event |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 111207 | Changed TSP to TO, removed requirement to have voice recording and expanded the requirement to have a satellite phone to all TOs. |

| Original Sponsor |  |
| --- | --- |
| Name | Dennis Starbuck on behalf of the ERCOT Black Start Task Force |
| E-mail Address | Dennis.starbuck@austinenergy.com |
| Company | Austin Energy |

Proposed Operating Guide Language Revision

### 4.6.5	Emergency Back Up Communication Facilities Criteria

Reference:  Protocol Section 6.4.2, Determination of ERCOT Control Area Requirements (In Part)

…(7)	Black Start Service: ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required.  ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC policy.

(1)	All back up communications system shall meet the following minimum requirements:

- (a)	Be operational for seventy-two (72) hours immediately following the start of a blackout without external power from the ERCOT grid;

- (b)	Provide direct voice communications between:  Black Start Resource and TO; TOs and appropriate TOs; TOs and ERCOT;

- (c)	Have written procedures that address operator training and the testing of the communication system; and,

- (2)	TOs shall have a satellite phone that meets the minimum back up communication requirements as a back up communication system and that is compatible with ERCOT’s satellite phone.