Recommendation for ERCOT Specific Requirements for Reliability Standards

11/12/07

- ERCOT shall monitor the following categories of performance and Compliance;

- Generation under-frequency relay coordination as specified in the Operating Guides for Generation Resources;

  - Testing and performance of governor under the Operating Guides, for Generation Resources;

(b) Written Black Start procedures, for QSEs that represent Generation Resources

- Power System Stabilizer (PSS) requirements, for QSEs and Generation Resources

  - Resource Response Monitoring Criteria for Frequency Disturbances

(1)	Each Resource must meet the following criteria when it is On-Line:

(a)	For all frequency deviations exceeding 0.1 Hz, ERCOT shall use recorded two-second scan rate values of real power output for each Resource to evaluate governor response or response to Dispatch Instructions. ERCOT shall use the recorded MW data beginning one minute before the start of the frequency excursion event or Dispatch Instruction until 20 minutes after the start of the frequency excursion event or Dispatch Instruction.  System performance is measured by comparing the actual Resource response to the frequency response capability requirements in the Operating Guides, using methods detailed therein.

(b)	ERCOT shall monitor energy that is delivered by a Resource during major frequency disturbances.

- ERCOT shall develop a TAC-approved TSP Monitoring Program to be included in the Operating Guides for TSPs.

(1)	Written Black Start procedures;