## Slide 1: ERCOT Wind Survey
Leo Villanueva

## Slide 2
Abilene
Mc Camey
Big Spring

## Slide 3
Far West

## Slide 4: Abilene Area All the values are based on returned ERCOT survey results
Total number of Wind Powered Generation Resources (WPGR) 16 (16)
Total max rated capacity – 2271 MW Average rated capacity – 142 MW
Average cut-off speed – 59 MPH
Average minimum wind speed at which generation starts – 8 MPH
Total rated reactive capability – 798 MVAr
Dynamic VAr control – 68% and Static VAr control – 32 %
Average number of turbines at each plant site – 98
37 % of the units in this area have feathering of the blades to control the output level (Based on the survey responses).

## Slide 5: Big Spring Area All the values are based on returned ERCOT survey results
Total number of WPGR’s 7 (7)
Total max rated capacity – 624 MW Average rated capacity – 89 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 181 MVAr
Dynamic VAr control – 43% and Static VAr control – 57 %
Average number of turbines at each plant site – 80
26 % of the units in this area have feathering of the blades to control the output level (Based on the survey responses).

## Slide 6: McCamey Area All the values are based on ERCOT returned survey results
Total number of WPGR’s 10 (7)
Total max rated capacity – 1791 MW Average rated capacity – 256 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 272 MVAr
Dynamic VAr control – 29% and Static VAr control – 71 %
Average number of turbines at each plant site – 168
29% the units have feathering of the blades to control the output level. (Based on the survey responses).

## Slide 7
Based on the returned survey results we have a total wind capacity of 4686 MW divided among 30 WPGR’s

## Slide 8
Region | Abilene (MVAr) | Big Spring (MVAr) | McCamey (MVAr)
Avg. Reactive Capability at 50% O/P | 33.14 | 10.788 | 21.71
Avg. Reactive Capability at 100% O/P | 49.25 | 15.775 | 38.85
Avg. Reactive Capability at no O/P | 9.05 | 6.029 | 0

## Slide 9: What is the VAR Capability required in the Interconnection Agreement?
Abilene: 6 WPGR’s said 0.95 pf leading or lagging. 2 WPGR said 0.98 pf leading or lagging. 8 said none.
Big Spring: All the WPGR’s said 0.95 pf leading or lagging.
McCamey: 4 WPGR’s said 0.97 pf leading and 1 said 0.96 leading. 2 said none.

## Slide 10: How far can units be backed down before operation becomes unstable (MW output or % of rated capability)?
Region | Abilene MW | Big Spring MW | McCamey MW
MW output after which operation becomes unstable | 0.069 | 0.057 | 0
5 WPGR’s in McCamey said Curtailment is achieved by stopping a group
of turbines (groups are predetermined and cycle through), not by reducing
Individual turbine output.

## Slide 11: Can individual turbines of this type be shut down at the facility on a routine basis (stop and start once per day)?
Abilene: 15 WPGR’s have the capability and 1 does not.
Big Spring: 7 WPGR’s have the capability of shutting individual turbines at the facility on a routine basis.
McCamey: 5 WPGR’s have the capability and 2 WPGR’s said that current control scheme does not shut down turbines but limit power output by modulating blade pitch.

## Slide 12: Are the facility turbines and control system and facility turbines able to provide automatic generation control (AGC) from a technical point of view? If not, would the turbines be capable of this if the control system was upgraded?
Abilene: 3 in Abilene area can provide AGC and 3 can provide with a control system upgrade.
Big Spring: 6 in Big Spring cannot provide automatic generation control (AGC). 1 can.
McCamey: 2 in McCamey area can provide Automatic Voltage Control whose set point is controlled by ERCOT.

## Slide 13: How flexible is the zero output reactive capability? For example, is it manually or automatically switched in? What are the issues associated with provided this reactive capability if requested by ERCOT in Real Time.
Abilene: 3 have static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically. 3 cannot provide any flexibility. 4 said wind dependant. 4 said they are automatically controlled by two controllers, but that could take some programming work to implement. 1 said automatically controlled between +9 or -9 MVAr. 1 WPGR’s VAr output is attributed to the capacitive nature of the underground collection system. Capability is limited due to underground cable splices and thermal backfill material.
Big Spring Area: 5 cannot have any flexible reactive capability at zero output. 1 has manual switching capability. 1 has static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically.
McCamey: None in McCamey area have flexible reactive capability at zero output.

## Slide 14
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Abilene:
Under voltage - 299vac at the turbine. Over voltage - 365vac at the turbine. Over frequency - 61hz at the turbine. Under frequency - 59hz at the turbine. 25vac asymmetry between phases at the turbine for 6 WPGR’s
Voltage 110 % nominal or < 70 % nominal for 1 WPGR
No response from 9 WPGR’s

## Slide 15: What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Big Spring Area:
90% ≤ System Voltage ≥ 110% ; 94% ≤ System Frequency ≥ 104% is the response from 2 WPGR’s
For a V-47 and a V-66 WTGL high voltage 500V sensed phase to ground, low voltage 340V sensed phase to ground; For a V-47: high frequency 60.4hz, low frequency 59.2hz; For a V-66: high frequency 60.3hz, low frequency 59.5hz.
Over Freq>61Hz for 0.5 s, Under Freq <=59 Hz Over Vol>120% is the response from 2 WPGR’s
Breaker trip for 1 WPGR

## Slide 16
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
McCamey:
Voltage 110 % nominal or < 70 % nominal for 1 WPGR for 2 WPGR’s
85% V & 0.1 sec TD 90% V & 5 sec TD 110% V & 60 sec TD 112% V & 0.1 sec TD for 1 WPGR’s
80% V & 0.2 sec TD 90% V & 60 sec TD 108% V & 5 sec TD 110% V & 0.2 sec TD for 4 WPGR’s

## Slide 17: What is the response time required to reduce output by 20%? (time from ERCOT notice to reduce to time when wind-ranch is 20% below previous output)?
Average response time for 10 WPGR’s in Abilene is 8 min. 6 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output.”
Average response time for Big Spring is 24 min.
Average response time for 2 WPGR’s in McCamey is 10 min. 5 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.

## Slide 18: What is the response time required to increase output by 20% (presuming wind available)? (time from ERCOT notice to increased to time when wind-ranch is 20% above previous output?
Average response time for 10 WPGR’s in Abilene is 8 min. 6 have a response of “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output.”
Average response time for 5 WPGR’s Big Spring is 21 min.3 WPGR’s have a response of “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output.”
Average response time for 2 WPGR’s in McCamey is 10 min. 5 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.

## Slide 19: When turbines are being controlled what is the available ramping capability assuming wind conditions and system transmission conditions that could accommodate full output? (ERCOT seeks to understand the ramping characteristics of the units and facility as a whole). Please describe (or provide output curves) on facility ramp rates and wind speed? (i.e. How long would it take to go from zero to 25% output? How long to go from 25 to 50% output? How long from 50 to 75% output and from 75% to 100% output?) Is the wind farm operating as designed? If not, why not?
Abilene: 0-25% (375kw) less than 1 minute;25-50% (750kw) less than 1 minute; 50-75% (1,125kw) less than 1 minute; 75-100% (1,500kw) less than 1 minute; 0-100% (1,500kw per unit) less than 4 minutes from 6 WPGR’s. 1 WPGR’s response is “Individual turbine can modulate from very low load levels to full load in about 2.5 minutes. Entire farm can modulate in about 5 minutes dependent on wind at each individual turbine location”. 1 WPGR said there are no ramp rates set and power of individual turbines can be quickly ramped down and park them as a whole when storms approach. 2 WPGR’s said “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output. Assuming there are perfect wind conditions then it would take approxiamately 5 minutes to bring the site up to full load (or 100% output)”.
Big Spring: There are no ramp rates. Everyone answered wind is the deciding factor for the output.
McCamey: 2 WPGR’s response is “Individual turbine can modulate from very low load levels to full load in about 2.5 minutes. Entire farm can modulate in about 5 minutes dependent on wind at each individual turbine location”. 5 WPGR’s response is “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output. Assuming there are perfect wind conditions then it would take approximately 5 minutes to bring the site up to full load (or 100% output)”.