ERCOT Operations Report

November 2007 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration |  |
| --- | --- | --- | --- |
| 11/2 9:17:30 | 59.85 | 6 s | 330 MW unit trip |
| 11/6 0:16:32 | 60.11 | 28 s | 1200 MW SCE Corrected |
| 11/6 22:06:12 | 59.85 | 1 m 22 s | 1500 MW SCE |
| 11/13 16:19:38 | 59.88 | 4 s | 580 MW unit trip |
| 11/15 0:11:16 | 60.11 | 24 s | Step increase in SCE. |
| 11/15 22:09:32 | 60.14 | 2 m 8 s | 3150 schedule change |
| 11/16 1:58:08 | 60.11 | 10 s | 660 MW SCE |
| 11/21 11:03:46 | 60.11 | 8 s | 500 MW SCE |
| 11/23 17:26:26 | 59.79 | 50 s | 775 MW unit trip |
| 11/24 8:55:04 | 59.83 | 8 s | 650 MW unit trip |
| 11/26 3:08:08 | 59.81 | 6 s | 650 MW unit trip |
| 11/30 5:30:34 | 60.11 | 16 s | 500 MW SCE |
| 11/30 18:01:24 | 60.12 | 1 m | Exhausted Down Regulation prior to ramp |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 11/2 9:17:28 | 11/2 9:39:52 | 0:22:24 | 600.38 |  |
| 11/2 22:58:06 | 11/2 23:08:56 | 0:10:50 | 320.54 | SCE |
| 11/6 0:10:26 | 11/6 0:19:54 | 0:09:28 | 330.73 | SCE |
| 11/6 22:00:58 | 11/6 22:29:56 | 0:28:58 | 595.30 |  |
| 11/7 20:02:12 | 11/7 20:13:08 | 0:10:56 | 340.90 | Tie schedule change. |
| 11/8 6:10:10 | 11/8 6:14:08 | 0:03:58 | 310.37 | SCE |
| 11/9 7:02:54 | 11/9 7:07:12 | 0:04:18 | 325.65 | SCE |
| 11/13 16:19:36 | 11/13 16:26:12 | 0:06:36 | 463.01 |  |
| 11/15 1:01:06 | 11/15 1:15:18 | 0:14:12 | 325.65 | SCE |
| 11/16 22:20:10 | 11/16 22:44:18 | 0:24:08 | 335.82 | Schedule change |
| 11/18 16:04:46 | 11/18 16:11:44 | 0:06:58 | 325.65 | SCE |
| 11/21 3:46:06 | 11/21 4:01:34 | 0:15:28 | 325.65 | SCE |
| 11/21 9:29:40 | 11/21 9:34:50 | 0:05:10 | 325.65 | SCE |
| 11/22 6:04:50 | 11/22 6:18:06 | 0:13:16 | 325.65 | SCE |
| 11/23 17:26:28 | 11/23 17:41:18 | 0:14:50 | 890.42 |  |
| 11/24 8:55:04 | 11/24 9:02:50 | 0:07:46 | 713.32 |  |
| 11/26 3:08:06 | 11/26 3:41:42 | 0:33:36 | 793.74 |  |
| 11/26 5:37:04 | 11/26 5:46:46 | 0:09:42 | 330.73 | SCE |
| 11/26 6:24:50 | 11/26 6:30:10 | 0:05:20 | 315.46 | SCE |
| 11/27 6:09:44 | 11/27 6:13:02 | 0:03:18 | 330.73 | Schedule change |
| 11/27 22:05:32 | 11/27 22:10:06 | 0:04:34 | 325.65 | Schedule change |
| 11/28 6:09:44 | 11/28 6:13:18 | 0:03:34 | 315.46 | SCE |
| 11/29 6:36:38 | 11/29 6:40:24 | 0:03:46 | 315.46 | Unit Trip |
| 11/29 17:39:18 | 11/29 17:45:26 | 0:06:08 | 330.73 | SCE |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 17 | 0 | 2 | 19 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 2 | 2 |
| DFW | 0 | 0 | 0 | 8 | 8 |
| E RIO | 0 | 2 | 7 | 0 | 9 |
| Houston | 0 | 24 | 2 | 3 | 29 |
| Laredo | 57 | 0 | 0 | 0 | 57 |
| North | 0 | 0 | 1 | 10 | 11 |
| Northeast | 0 | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 1 | 3 | 12 | 16 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 23 | 8 | 0 | 31 |
| Western | 0 | 6 | 27 | 31 | 64 |
|  | 57 | 73 | 48 | 68 | 246 |

| Historical Totals | Nov-06 | Oct-07 | Nov-07 |
| --- | --- | --- | --- |
| Austin | 19 | 45 | 19 |
| Bryan Area | 0 | 1 | 0 |
| Corpus | 0 | 0 | 2 |
| DFW | 3 | 16 | 8 |
| E RIO | 12 | 10 | 9 |
| Houston | 1 | 44 | 29 |
| Laredo | 66 | 71 | 57 |
| North | 1 | 26 | 11 |
| Northeast | 2 | 1 | 0 |
| San Antonio | 4 | 18 | 16 |
| South | 5 | 0 | 0 |
| W RIO | 80 | 15 | 31 |
| Western | 19 | 17 | 64 |
| Total | 212 | 264 | 246 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

Zonal OC1

| CSC | Days |
| --- | --- |
| North - Houston | 13 |
| West - North | 10 |
| North - West | 1 |
| South - North | 1 |

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Morgan Creek - Quail Switch & Odessa | Big Springs Sw - Big Spring West | 19 |
| Valley Import |  | 4 |
| Fisher Road - Oklaunion & Bowman | Bomarton - Seymour 69 kV | 3 |
| Calaveras Facility - Ball Park 138 kV | Westside CPS - Five Points 138 kV | 3 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Lake Creek - Temple Pecan Creek | 3 |
| Martin Lake SES - Tricorner 345 kV | planned outage stability limit | 2 |
|  | Midtown - Garrot Lane 138 kV | 2 |
| Fort Mason 138/69 kV Transformer | Mena 138/69 kV Transformer | 2 |
| Temple Pecan Creek - Tradinghouse - Temple Switch 345 kV | Goldthwaite 138/69 kV auto | 2 |
| Allen Switch - Royse Switch & Monticello | Schroeder - Dallas TI 138 kV | 1 |
| Lon Hill - North Edinburg 345 kV | Rio Hondo - Nelson Sharpe 345 kV | 1 |
| Lon Hill - North Edinburg 345 kV | Lon Hill - Nelson Sharpe 345 kV | 1 |
| Jewett - TH Wharton & Tomball 345 kV | Watson Chapel - Robertson 138 kV | 1 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Watson Chapel - Robertson 138 kV | 1 |
| Comanche Peak SES - Decordova SES and Wolf Hollow - Rocky Creek 345 kV | Concord 345/138 kV Autotransformer | 1 |
| Comanche Peak units 1 & 2 345 kV | Austrop - Sandow Switch 345 kV | 1 |
| La Palma 138/69 kV Auto 1 | La Palma 138/69 kV Auto 2 | 1 |
| Morgan Creek 345/138 kV Auto 2 | Morgan Creek 345/138 kV Auto 1 | 1 |
| San Miguel - Dilley Switch 138 kV | Derby - Pearsall 69 kV | 1 |
| South Channel - Jefferson 138 kV | Jefferson - Crown 138 kV | 1 |
| South Lane City - Lane City 138 kV | New Gulf -Texas Gulf Sulphur | 1 |
| STP - Hilje - White Point 345 kV | Blessing - Lolita 138 kV | 1 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | West - Lorena 69 kV | 1 |
| Sandow Switch - Sandow SES 138 kV | Sandow SES 345/138 AT-1 | 1 |
| Trindad - Stryker Creek & Mt. Enterprise | Elkton - Athens Tap 138 kV | 1 |
| Garfield - Lytton Springs 345 kV | Lytton Springs - Pilot Knob 138 kV | 1 |
| Midland East - Odessa EHV 345 kV | Odessa Southwest - Moss Switch | 1 |
| Bluff Creek - Horse Hollow | planned transmission outage | 1 |

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 11/01/2007 | Operating Period Desk | 353 |
| 11/01/2007 | Transmission & Security Desk VDI - JOU | 352 |
| 11/01/2007 | Frequency Control Desk VDI - JOU | 351 |

EECP

11/29 06:48	EECP Step 1 initiated.

Communication

11/3  11:35 – 14:00  Issued a Market Notice for  Day Ahead Ancillary Market close extended to 14:00.   DST issues.

11/5 16:15  RPRS failed to solve.  Adjustment period RPRS Market opened at 18:45.

11/9 Held interval 07:30 through 08:30.  Real- Time Balancing Market failed to clear.

11/29  Held 09:45 interval for a CSC limit change.

## ERCOT peak (Unofficial)

11/26 08:00  39,500 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |
| --- | --- | --- | --- |
| MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
| 2006 | 2006 | 2007 |  |
| January | 4.79 | 4.55 |  |
| February | 4.81 | 3.75 |  |
| March | 4.95 | 2.7 |  |
| April | 5.59 | 3.002 |  |
| May | 3.59 | 3.22 |  |
| June | 2.65 | 4.46 |  |
| July | 2.62 | 4.29 |  |
| August | 2.09 | 3.11 |  |
| September | 4.03 | 3.781 |  |
| October | 3.63 | 3.08 |  |
| November | 3.28 | 2.95 |  |
| December | 3.44 | NA |  |
| Annual Average | 3.79 | 3.54 |  |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event | Event |
| --- | --- | --- | --- | --- |
| 11/01 | 5:02 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/01 | 16:04 | 23:45 | Alert | ARR below 2500 MW. |
| 11/02 | 0:15 | 20:00 | Advisory | ARR below 3000 MW. |
| 11/03 | 0:10 | 6:06 | Advisory | ARR below 3000 MW. |
| 11/03 | 9:35 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/04 | 0:15 | 2:50 | Advisory | ARR below 3000 MW. |
| 11/04 | 12:47 | 20:05 | Advisory | ARR below 3000 MW. |
| 11/05 | 6:36 | 19:25 | Advisory | ARR below 3000 MW. |
| 11/06 | 0:05 | 21:36 | Advisory | ARR below 3000 MW. |
| 11/06 | 0:55 | 11:36 | Alert | ARR below 2500 MW. |
| 11/06 | 17:45 | 21:36 | Alert | ARR below 2500 MW. |
| 11/06 | 23:02 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/07 | 0:15 | 14:30 | Advisory | ARR below 3000 MW. |
| 11/07 | 16:20 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/07 | 17:46 | 20:30 | Alert | ARR below 2500 MW. |
| 11/08 | 14:24 | 22:30 | Advisory | ARR below 3000 MW. |
| 11/09 | 4:45 | 18:30 | Advisory | ARR below 3000 MW. |
| 11/13 | 6:32 | 22:35 | Advisory | ARR below 3000 MW. |
| 11/15 | 6:35 | 23:59 | Advisory | ARR below 3000 MW. |
| 11/16 | 23:06 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/17 | 0:01 | 0:07 | Advisory | ARR below 3000 MW. |
| 11/17 | 8:48 | 22:15 | Advisory | ARR below 3000 MW. |
| 11/18 | 8:42 | 21:00 | Advisory | ARR below 3000 MW. |
| 11/18 | 18:14 | 20:00 | Alert | ARR below 2500 MW. |
| 11/19 | 9:37 | 19:06 | Advisory | ARR below 3000 MW. |
| 11/20 | 0:15 | 4:00 | Advisory | ARR below 3000 MW. |
| 11/20 | 13:11 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/20 | 16:24 | 20:00 | Alert | ARR below 2500 MW. |
| 11/21 | 0:15 | 20:00 | Advisory | ARR below 3000 MW. |
| 11/21 | 4:31 | 6:03 | Alert | ARR below 2500 MW. |
| 11/21 | 9:50 | 13:08 | Alert | ARR below 2500 MW. |
| 11/22 | 0:15 | 0:30 | Advisory | ARR below 3000 MW. |
| 11/22 | 8:45 | 24:00 | Advisory | ARR below 3000 MW. |
| 11/23 | 0:00 | 11:00 | Advisory | ARR below 3000 MW. |
| 11/23 | 17:29 | 23:49 | Advisory | ARR below 3000 MW. |
| 11/24 | 8:30 | 22:00 | Advisory | ARR below 3000 MW. |
| 11/25 | 4:22 | 06:45 | Advisory | ARR below 3000 MW. |
| 11/25 | 17:33 | 23:05 | Advisory | ARR below 3000 MW. |
| 11/26 | 5:22 | 10:00 | Advisory | ARR below 3000 MW. |
| 11/26 | 6:42 | 9:01 | Alert | ARR below 2500 MW. |
| 11/27 | 6:56 | 8:20 | Advisory | ARR below 3000 MW. |
| 11/28 | 6:24 | 21:00 | Advisory | ARR below 3000 MW. |
| 11/29 | 4:05 | 15:10 | Advisory | ARR below 3000 MW. |
| 11/29 | 6:28 | 9:00 | Alert | ARR below 2500 MW. |
| 11/29 | 6:48 | 8:15 | EECP | ARR below 2300 MW. |
| 11/29 | 17:45 | 19:45 | Advisory | ARR below 3000 MW. |
| 11/30 | 17:35 | 24:00 | Advisory | ARR below 3000 MW. |

Transmission

11/3  21:45 – 11/4 02:00	Transmission Emergency for load shed in Nueces County to mitigate the loss of the Airline 138/69 kV transformer #1.

11/27  09:30 – 17:00  	Transmission.  Loss of Oklaunion - Bowman Switch 345 kV loads Southwest Vernon 138/69 kV transformer.

Other

11/14	Conducted Winter Storm Drill.