## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification, Version 1.0
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | GP&L (R.Hoeinghaus) |  | Title Page |  |  | GP&L Comment: Only comment is that we believe that this is a well written document – good job | Accepted | J. Dondeti
2 | NRG (D.S.Mai) | 6 | 1.2 |  |  | The objectives of these this requirements specification is are to: | Accepted | J. Dondeti
3 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | (deleted space between "with" and "in") The scope of EMS is described using a block diagram of various functions with in the EMS and description of the processes conducted within the EMS, as they relate to the Texas Nodal market. | Accepted | J. Dondeti
4 | Brazos Electric (T.Kroskey) | 8 | 2.1.1 |  |  | (deleted space between "with" and "in") The diagram in Figure 1: EMS Functional Diagram depicts various functions with in the EMS. | Accepted | J. Dondeti
5 | NRG (D.S.Mai) | 8 | 2.1.1 |  |  | (deleted space between "with" and "in") The scope of EMS is highlighted, and the sub-systems with in EMS and the data interfaces to the external systems are identified. | Accepted | J. Dondeti
6 | NRG (D.S.Mai) | 10 | 2.1.2.1 |  |  | A. Outage Coordination Evaluation – EMS addresses the tools required for the evaluation of Transmission and Generation Facilities outages. The Outage Evaluation sub-system within EMS will provide necessary tools to the ERCOT outage coordinators to analyze system security, and cost impacts under outage conditions. The requirements for Outage Evaluation sub-system are specified in the Texas Nodal EMS Outage Evaluation Requirements Specification document. The functions with in Outage Evaluation sub-system are described below: | Accepted | J. Dondeti
7 | NRG (D.S.Mai) | 10 | 2.1.2.1 |  |  | A. Outage Coordination Evaluation – EMS addresses the tools required for the evaluation of Transmission and Generation Facilities outages. The Outage Evaluation sub-system within EMS will provide necessary tools to the ERCOT outage coordinators to analyze system security, and cost impacts under outage conditions. The requirements for Outage Evaluation sub-system are specified in the Texas Nodal EMS Outage Evaluation Requirements Specification document. The functions with in Outage Evaluation sub-system are described below: ... Note: does this function also support the evaluation of RMR service? | Clarification Provided | J. Dondeti | No it does not.
8 | NRG (D.S.Mai) | 11 | 2.1.2.1 |  |  | (deleted space between "with" and "in") B. Load Forecasting … The functions with in Load Forecasting sub-system are described below: | Accepted | J. Dondeti
9 | NRG (D.S.Mai) | 11 | 2.1.2.2 |  |  | A. Wind-Powered Generation Resource Production Potential i. RPP – This function includes a Wind Power Forecasting service and a set of interfaces to exchange data with the service provider. Collectively the WGRPP is created and communicated to the QSEs via MIS. LTWPF is used in Outage Evaluation and other future security and stability studies, to support the Management Activities for the ERCOT System on a rolling 12-month basis. The requirements for the Wind Power Forecasting sub-system are specified in the Texas Nodal EMS Requirements Specification For Wind Power Forecasting document. | Accepted | J. Dondeti
10 | TXU (B.Spangler) | 14 | 2.1.2.4 |  |  | C. Voltage Support Services i. Real-Time Voltage Support – This function provides tools to recommend reactive device switching and minimizes the dependence on generation-supplied reactive resources. The requirements for real-time voltage support functions are described in Texas Nodal EMS Voltage Support Requirements Specification document. {TXU Comment: Both EMS and MMS have a role to play in the collection of relevant real-time data for purposes of Settlement. It is not clear how this role is addressed within the existing EMS/MMS Business Requirements Documentation. For example, for the purpose of calculating the SPP in each of the regular 15 min Settlement Intervals within a Real Time hour the number of SCED runs, the time duration for the LMPs for each SCED run, and the registration of each time sequence (SCED execution and clock time) must be accomplished. Please explain how these elements will be accomplished. Is there a need for a separate process to address these needs?} | Clarification Provided | J. Dondeti | Move to IDA Punch List.
11 | NRG (D.S.Mai) | 15 | 2.1.3 |  |  | Out of Scope Items for EMS … D. Data Collection – Defining what data is required for market monitoring and compliance is out of scope for the EMS project team. EMS data specifically identified by the Nodal protocols as required for reporting or retention will be identified by the EMS project team and provided to EDW or PI with retention and reporting instructions, and is in scope. Providing data sets specifically identified by other project teams is in scope. Note: is PI a separate system, or a sub-system of EMS? | Clarification Provided | J. Dondeti | Move to IDA Punch List.
12 | NRG (D.S.Mai) | 15 | 2.2 |  |  | As with any system, in general EMS is dependant on the input data from various sources. Specifically EMS is dependant on receiving Network Operation Model from NMMS, SCADA/ICCP Telemetry from MPs, Weather Data from ERCOT designated weather service provider, Real Time Dispatch data from MMS, Scheduled Outages from Outage Scheduler. | Accepted | J. Dondeti
13 | TXU (B.Spangler) | 15 | 2.2 |  |  | A key assumption for EMS is that with the upload of Network Operation Model on a daily basis into EMS real-time functions, the usage of appropriate Network Operation Model in the EMS study functions is feasible. {TXU Comment: Just exactly what is this paragraph saying? Is the concern about NMMS functionality? Please provide more detail.} | Clarification Provided* | J. Dondeti | Delete this assumption. Data model requirements cover the assumption regarding the testing of the Network Operations Moel.
14 | Brazos Electric (T.Kroskey) | 19 | 4.1 | EMS-SR10 |  | (added one space after "7.1") Subsequent to the initial presentation of a display, the data on the display shall be updated at the rates specified in Section 7.1 and also within the display response time requirements shown in Section 7.2. | Accepted | J. Dondeti
15 | Brazos Electric (T.Kroskey) | 20 | 4.2 | EMS-SR13 |  | Description: The EMS systems functions shall comply with any requirements specified in the following NERC Reliability Standards applicable to ERCOT: | Accepted | J. Dondeti
16 | Brazos Electric (T.Kroskey) | 21 | 4.3 | EMS-SR16 |  | Description: The EMS functions shall provide information described in functional requirements documents forto all defined systems components. The EMS supplier is required to assists and to provide assistance and the necessary integration services in collaboration with other systems components designers and implementers. | Accepted | J. Dondeti
17 | Brazos Electric (T.Kroskey) | 21 | 4.3 | EMS-SR17 |  | Description: Impacts to EMS database structures, tables, and the views shall be identified and included in the EMS supplier work effort estimates. All existing EMS tables and database views that will be modified shall be identified in the EMS supplier solution. All new tables and database views shall be identified in the supplier’s specific EMS supplier function solution. | Accepted | J. Dondeti
18 | Brazos Electric (T.Kroskey) | 22 | 4.4 | EMS-SR18 |  | Description: The EMS functions and all equipment supplied and connected to the EMS networks described in the EMS Requirements Specifications will be considered Critical Cyber Assets as defined by NERC Standard CIP-002. The supplier’s processes and supplied system shall complyconfirm at a minimum to all applicable requirements of the Critical Infrastructure Protection standards promulgated by the North American Reliability Council, including: 1) CIP-005 Electronic Security. The EMS software shall be audited immediately prior to delivery to insure that ERCOT required standards for cyber security are satisfied. | Accepted | J. Dondeti
19 | Brazos Electric (T.Kroskey) | 22 | 4.4 | EMS-SR20 |  | Description: In the event that a component of the EMS is damaged or performance degraded due to a cyber security incident, the affected component must be able to be rapidly isolated from the rest of the EMS, and the function restored in a timely manner. The EMS supplier shall provide a process or procedure that would be followed in this event. | Accepted | J. Dondeti
20 | Brazos Electric (T.Kroskey) | 22 | 4.4 | EMS-SR21 |  | Description: The EMS supplier shall ensure that aAll applications, utilities, system services, scripts, configuration files, databases, user accounts and all other software not required for operation of the EMS shall be removed by the supplier prior to commissioning. The items to be removed shall specifically include: | Accepted | J. Dondeti
21 | Brazos Electric (T.Kroskey) | 23 | 4.4 | EMS-SR22 |  | Description: Additional security “hardening”, following established methods and guidelines, developed by the original software vendor, the US Government National Institute of Standards and Technology, The US Government Department of Defense, the US Government Department of Energy, or similar recognized organizations shall be provided by the EMS vendor subject to ERCOT’s approval. | Accepted | J. Dondeti
22 | Brazos Electric (T.Kroskey) | 24 | 4.4 | EMS-SR25 |  | Description: The EMS supplier shall provide a mechanism for periodically scanning the integrity of the software on the EMS disks to determine if unauthorized modifications to the software have been made. A third party tool may be used for this function. The process of making an authorized modification to the software must include an update to the integrity database to ensure that the scanning tool does not detect valid or authorized changes as unauthorized. The scanning software shall be configurable by ERCOT to run manually or periodically, and shall not interfere with the performance or operation of the EMS or any application. | Accepted | J. Dondeti
23 | Brazos Electric (T.Kroskey) | 24 | 4.4 | EMS-SR26 |  | Description: Where technically feasible and where appropriate commercial products exist (e.g., Microsoft Windows environments), the EMS supplier shall implement anti-virus, spyware, and other malware detection systems. These products shall be installed and running throughout the development, test, commissioning and acceptance of the system to ensure that their performance impact is known and tested. The EMS vendorContractor shall provide procedures for the secure updating of configuration and signature files to ensure that the tools remain current with updates and releases. | Accepted | J. Dondeti
24 | Brazos Electric (T.Kroskey) | 25 | 4.4 | EMS-SR29 |  | Description: The EMS shall generate an alarm when access activity may be indicative of attempts to obtain unauthorized access to system services or data. A simple method shall be provided for the user to view and to change the rules for generating alarms. Initially, an alarm shall be generated when the system detects the any of following activities: | Accepted | J. Dondeti
25 | Brazos Electric (T.Kroskey) | 27 | 4.5 | EMS-SR35 |  | (added period at end of bullet) 4. Alarm, event, and summary displays (such as off-normal, control inhibit, and alarm inhibit displays) or sufficient information to rebuild the displays in their entirety (including the time and date of the entry, not the time and date the display was created). | Accepted | J. Dondeti
26 | Brazos Electric (T.Kroskey) | 27 | 4.5 | EMS-SR36 |  | Description: All processors, devices, and functions shall be monitored for fatal and recoverable errors. All detected errors and failures shall be recorded for maintenance purposes, and all errors should generatethrow SNMP traps. These records shall include the dates and times of the failures, the reason for the failure, and of the subsequent automatic or manual return to service. | Accepted | J. Dondeti
27 | Brazos Electric (T.Kroskey) | 28 | 4.5 | EMS-SR39 |  | Description: In a complex system such as an EMS, unreasonable results are expected to occasionally occur. In order to prevent this from having a harmful effect on the EMS, all data shall be checked by the EMS for reasonability. All input data and parameters, whether collected automatically or entered by a user, shall be checked by the EMS for reasonability and rejected if they are unreasonable. All intermediate and final results shall be checked by the EMS to prevent unreasonable data from being propagated or displayed to the user. When unreasonable input data or results are detected, diagnostic messages, clearly describing the problem, shall be generated by the EMS. All programs and the system shall continue to operate in the presence of unreasonable data. Upon the declaration of data as unreasonable, all calculations using the unreasonable data shall be temporarily suspended or continue to use the last reasonable data. | Accepted | J. Dondeti
28 | Brazos Electric (T.Kroskey) | 28 | 4.5 | EMS-SR40 |  | (inserted linespace between paragraphs) Once initiated, the distributed backup and archiving services shall automatically back up all information needed to recover from failures or data corruption without manual intervention by users, except for replenishment of removable media. Although the devices being backed up may be physically separate, the backup system shall be managed centrally. At the option of the user, the backup shall be encrypted or otherwise secured from unauthorized use. | Accepted | J. Dondeti
29 | TXU (B.Spangler) | 32 | 4.6 | EMS-SR53 |  | Description: Except for communications with data sources and other computer system connected to the EMS by the IS WAN {TXU Comment: Define the “IS WAN”} or the Control Center WAN, failed devices shall be reinstated by user command only. Failed communications to data sources or computer systems connected to the EMS by the IS WAN and the Control Center WAN shall be periodically retried. When reliable communications are reestablished, the RTU, data source, or communication channel shall be automatically returned to operation. | Accepted | J. Dondeti
30 | Brazos Electric (T.Kroskey) | 33 | 4.6 | EMS-SR55 |  | Description: ERCOT will normally operate the EMSpower system with users at both the TCC and ACC. Assuming that the PCS is operating in the in-control mode and the SCS is operating in the reserve mode, in the event the PCS becomes inoperable, the SCS will be brought into service. In the event that either center must be abandoned, the users at the other center will assume full responsibility for power system operation and the system at that center will be brought into service (if not already in service). | Accepted | J. Dondeti
31 | Brazos Electric (T.Kroskey) | 35 | 4.8 | EMS-SR59 |  | ERCOT recognizes that the documentation scheme used by the vendorContractor may not match that described in this and other sections. However, the documentation supplied shall provide all of the information described in the remaining requirements of this section. | Accepted | J. Dondeti
32 | TXU (B.Spangler) | 35 | 4.8 | EMS-SR59 |  | ERCOT recognizes that the documentation scheme used by the Contractor may not match that described in this and other sections. However, with the approval of ERCOT, the Contractor may supply alternative documentation suppliedprovided that, in ERCOT’s sole discretion such documentation, shall the Contractor supplied documentation provides all of the information described in the remaining requirements of this section. {TXU edits: The edits are required to clearly delineate the decision authority concerning the content of the documentation.} | Accepted | J. Dondeti
33 | Brazos Electric (T.Kroskey) | 36 | 4.9 | EMS-SR64 |  | Description: The delivered software shall provide and support exception handling, error detection and diagnostic tools sufficient to support the functional requirements to ERCOT’s satisfaction. User and operator software messages shall be formatted in plain English and generated at the application level and not at the OEM software level (ORACLE, UNIX, etc.) . Error messages will provide the viewer with clear information about the error and steps to remediate it. ERCOT will review and approve all error messages. | Accepted | J. Dondeti
34 | Brazos Electric (T.Kroskey) | 36 | 4.9 | EMS-SR65 |  | In addition to the application specific alarms, the alarm system shall be able to report system conditions: 1. An application function is missing intervals, or running significantly slower than usual i.e. function execution time is more than its maximum execution time required under high activity, which might be a tunable system parameter. 2. Utilization of CPU processing for a single application task exceedsbeats the limit (say 35%) under steady state condition. 3. Disk space is full or running out. | Accepted | J. Dondeti
35 | Brazos Electric (T.Kroskey) | 36 | 4.9 | EMS-SR66 |  | Description: The Alarm sub-system of the EMS must be customized and configured by the vendor to meet ERCOT needs. Vendor shall work with ERCOT during the detailed design phase to identify the alarms that are not applicable to ERCOT EMS and, the various attributes of all the alarms required in the ERCOT EMS. | Accepted | J. Dondeti
36 | Brazos Electric (T.Kroskey) | 37 | 5 |  |  | This requirements document primarily addresses Supplemental Requirements and therefore there protocol coverage is not provided. | Accepted | J. Dondeti
37 | Brazos Electric (T.Kroskey) | 38 | 6.1 |  |  | Critical Data Points: A SCADA point which if invalid (bad telemetry or unavailable?)renders a portion of the Transmission System unnobservable. | Clarification Provided* | J. Dondeti | Will update to read "unavailable"
38 | Brazos Electric (T.Kroskey) | 38 | 6.2 |  |  | 6. 2 Acronyms and Abbreviations ... ICCP: Inter-Control Center Communications Protocol (TASE.2) IT WAN: ERCOT corporate wide area network | Accepted | J. Dondeti
39 | NRG (D.S.Mai) | 40 | 7 |  |  | 7. Attachments Note: is there a dimensionality or sizing requirement document specifying the EMS System Sizing Parameters (maximum number of status points, analog points, generating units, etc.)? | Clarification Provided* | J. Dondeti | Yes. We will add it in the appendix of this document.
40 | NRG (D.S.Mai) | 40 | 7.1 | Attachment 1 |  |  | Accepted | J. Dondeti
41 | NRG (D.S.Mai) | 40 | 7.1 | Attachment 1 |  | 7.1 Attachment 1 – Function Periodicity and Execution Time … Note: what are the requirements for the daily upload of Network Operation Model into EMS real-time functions (the upload mentioned in section 2.2)? | Clarification Provided* | J. Dondeti | Document will be updated to provide details. EMS data model doc contains this info.
42 | Brazos Electric (T.Kroskey) | 43 | 7.6 | Attachment 6 |  | System Activity Scenarios – Base Condition ... 4. The contents of the EMS databases used for performance validation shall be as determined by ERCOT. The size databases sizes used in the performance validation will not be greater than the EMS delivered capacity. | Accepted | J. Dondeti
43 | Brazos Electric (T.Kroskey) | 44 | 7.6 | Attachment 6 |  | (added period; deleted comma; added "and") System Activity Scenarios – Steady State Scenario Description: The steady state scenario shall consist of the base conditions and the following activities over a 60-minute period. During the test all LFC deployments shall be completed within <2 seconds, , each SCADA override will complete within 1 second, each outage evaluation study will complete a 24 hour case (24 study scenarios) within 30 minutes, and : 1. At-least twenty-five percent of all the analog points in the test database shall change sufficiently each time they are acquired so as to require complete processing by the EMS. 2. Thirty alarms per minute (fifteen status alarms and fifteen analog alarms) shall be generated and processed. Each of these alarms may be acknowledged within sixty seconds at ERCOT’s discretion. 3. One new display shall be called into one of the windows at each console every sixty seconds. | Accepted | J. Dondeti
44 | Brazos Electric (T.Kroskey) | 45 | 7.6 | Attachment 6 |  | System Activity Scenarios – Steady State Scenario ... 12. One query of the current conditions for data from the continuous data recording function data from one-half of the manager consoles every two minutes. The queries shall total no more than 2000 data items per minute. | Accepted | J. Dondeti
45 | Brazos Electric (T.Kroskey) | 45 | 7.6 | Attachment 6 |  | (added period; deleted "<"; added "and"; added space after "30") System Activity Scenarios – High Activity Scenario Description: The high activity scenario shall consist of the base conditions and the following activities over a 60-minute period. During the test all LFC deployments shall be completed within <4 seconds, each SCADA override will complete within 5 seconds, each outage evaluation study will complete a 24 hour case (24 study scenarios) within 30 minutes, and : 1. At-least fifty percent of all the analog points in the test database shall change sufficiently each time they are acquired so as to require complete processing by the EMS. ... 7. The LFC shall be executed on a 4 second basis and 30 percent of the generators shall be under regulation control. ... | Accepted | J. Dondeti
46 | Brazos Electric (T.Kroskey) | 46 | 7.6 | Attachment 6 |  | System Activity Scenarios – High Activity Scenario ... 11. One query of the current conditions for data from the continuous data recording function data from one-half of the manager consoles every two minutes. The queries shall total no more than 2000 data items per minute. | Accepted | J. Dondeti

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.