## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Dynamic Ratings, Version 1.0
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment | Revised Reason / Comment
1 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All Dynamic Ratings requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Functional Diagram that describes Dynamic Ratings. | Accepted | J. Dondeti | The supplimental requrements are not mapped to the Functional Diagram. So, we agree.
2 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | The primary purpose of Dynamic Ratings is to improve the economic efficiency of the market by reflecting the change in ambient weather conditions on the ratings of TSP designatedkey transmission elements. | Accepted | A. Boecker | Comment accepted as is.
3 | CNP (E.John) | 9 | 2.3 |  |  | 1. We assume that the nodal protocol Section 3.10.8.3, requiring assuming the automatic implementation of new dynamic ratings within 24 hours will be performed by NMMS and is outside the scope of these requirements. | Accepted | A. Boecker | Comment accepted as is.
4 | Brazos Electric (T.Kroskey) | 10 | 3.1 |  |  | …. The respective source system shall make the data available to Dynamic Ratings Processor through interfaces to be identified in the design process. | Accepted | J. Dondeti | Protocols distinguish between Dynamic Ratings and the Dynamic Ratings Processor. So, we agree.
5 | CNP (E.John) | 10 | 3.1 | DR-FR1 |  | B. Dynamic Ratings shall use the following real-time input data, provided by TSPs via ICCP and obtained from SCADA: i. MVA ratings: Normal Rating, Emergency Rating, and 15-Minute Rating, for a subset of Transmission Elements. It is assumed here that a TDSP is allowed to have a mix of the three SCADA methods for portions of it’s lines. If not, then the requirements should implicitly included that capability. | Clarification Provided* | A. Boecker J. Dondeti | Requirements will be updated to clarify that each TSP can have any combination of the three types of real-time input for Dynamic Ratings. Each Transmission Element's Dyanmic Rating will be calculated in one of the three methods. CRR Dynamic Ratings: We need add a IDA punch list item to ensure that EMS and CRR are using the same source and methodology to compute Dynamic Ratings. | Added a statement that a transmission provider may use any of the 4 methods listed for each transmission element . Added an item to the IDA a punch list to ensure the EMS and CRR using the same source and methodology to compute dynamic ratings .
6 | Brazos Electric (T.Kroskey) | 11 | 3.1 | DR-FR1 |  | … static table changes with in an hour ... | Accepted | A. Boecker | Editorial comment.
7 | CNP (E.John) | 11 | 3.2 | DR-FR2 |  | Description: A. Dynamic Ratings Processor shall be executed every 10 seconds (Should this be “Minutes”? ) to update real-time ratings. This real-time execution periodicity shall be configurable. | Clarification Provided* | J. Dondeti | Protocl requirement is that the TSPs provide rating updates once every ten minutes (3.10.8.5). Protocols also require ERCOT to use the ratings with in five minutes of receipt (3.10.8.2 (2)). In order to ensure all the information provided by TSPs, possibly at different time instances, is processed the Dynamic Ratings Processor needs to be executed more often than 5 minutes. We will change the requirements to read "5 minutes."
8 | Brazos Electric (T.Kroskey) | 11 | 3.2 | DR-FR2 |  | Description: A. Dynamic Ratings Processor shall be executed every 10 seconds to update real-time ratings. This real-time execution periodicity shall be configurable by an Applications Administrator. B. Dynamic Ratings Processor shall be executed every hour, a few minutes after weather forecast from the weather service provider is obtained, to update future dynamic ratings. This execution periodicity and the execution timing shall be configurable by an Applications Administrator. | Clarification Provided | A. Boecker | For "Application Administrator" we may come-up with a common terminology across the systems or define a new term, and update the requirements accordiningly. IDA Punch List. Timing of input to HRUC. | Added an issue tothe IDA punch list address the timing of input to the HRUC process.
9 | Brazos Electric (T.Kroskey) | 12 | 3.2 | DR-FR3 |  | Description: A. Dynamic Ratings Processor shall calculate for each periodic execution the real-time dynamic ratings as follows based on the method specified on the Transmission Element: … iii. .... If the telemetered temperature is in between the temperature points in the static table, then the ratings shall be calculated by interpolating between the points. ... … C. Dynamic Ratings Processor shall validated the ratings calculated using telemetry, as follows: … ii. If the difference is more than a configurable threshold set be an Applications Administrator, then … iii. Dynamic Ratings shall further be compared with the nominal ratings. If the difference is more than a configurable threshold set be an Applications Administrator then nominal ratings shall be used instead of the calculated ratings. | Clarification Provided | A. Boecker | For "Application Administrator" we may come-up with a common terminology across the systems or define a new term, and update the requirements accordiningly. C (iii) IDA Punch List. Operations define a process in form of an NPRR before this is made a requirement. Remove this requirement to be in agreement with protocols. Consider the last good value. | Deleted requirement C (iii) and added to IDA punch list to address this issue .
10 | CNP (E.John) | 12 | 3.2 | DR-FR3 |  | C. Dynamic Ratings Processor shall validated the ratings calculated using telemetry, as follows. … ii. If the difference is more than a configurable threshold, then a The ratings calculated using the temperature from weather service provider shall be used as the Dynamic Ratings if authorized by the TDSP, otherwise the nominal ratings should be used.. | Accepted | A. Boecker | Comment accepted as is.
11 | Brazos Electric (T.Kroskey) | 13 | 3.2 | DR-FR5 |  | B. The rating deviation shall be averaged for hourly, daily, and monthly rating deviations for the normal, emergency, and 15-minute ratings for each Transmission Element. | Accepted | A. Boecker | Comment accepted as is.
12 | CNP (E.John) | 13 | 3.2 | DR-FR6 |  | A. Dynamic Ratings for future hours shall be calculated as follows: … iii. If the telemetered forecasted (Was this meant to say forecasted in stead of telemetered?) temperature is in between the temperature points in the static table, then the ratings shall be calculated by interpolating between the points. If the telemetered forecasted temperature is outside the temperature points in the static table, then the ratings shall be set to the boundary point ratings. | Accepted | A. Boecker | Comment accepted as is.
13 | Brazos Electric (T.Kroskey) | 14 | 3.2 | DR-FR6 |  | B. For all future hours, Dynamic Ratings Processor shall use corresponding future data models, including the static table. … | Accepted | A. Boecker | Protocols distinguish between Dynamic Ratings and the Dynamic Ratings Processor. So, we agree.
14 | Brazos Electric (T.Kroskey) | 15 | 3.2 | DR-FR8 |  | Description: A. Dynamic Ratings Processor shall allow ERCOT operator to manually update any SCADA telemetered input: Transmission Element MVA ratings, Transmission Element ampere ratings, and Weather Zone temperature. B. Dynamic Ratings Processor shall provide a summary display of telemetered data for each type of input data for ERCOT operator to view and update suspect data. | Accepted | A. Boecker | Protocols distinguish between Dynamic Ratings and the Dynamic Ratings Processor. So, we agree.
15 | Brazos Electric (T.Kroskey) | 15 | 3.4 | DR-FR10 |  | C. The above data shall be available in online for four years, and stored for seven years. | Accepted | A. Boecker | Comment accepted as is.
16 | Brazos Electric (T.Kroskey) | 16 | 3.5 | DR-FR11 |  | Description: … C. No later than 0600 in the Day-Ahead, Dynamic Ratings Processor shall make the next 120 hours weather data assumptions used by ERCOT available to MIS to post a report on the MIS Secure Area. D. Average monthly rating deviation shall be posted on MIS for the normal, emergency, and 15-minute ratings for each Transmission Element. | Accepted | J. Dondeti | Accept comment as-is.
17 | Brazos Electric (T.Kroskey) | 17 | 4 | DR-SR1 |  | Description: There shall be no degradation in the performance of ERCOT systems as a result of the Dynamic Ratings Processor functions execution under full volume processing. For all EMS applications using the Dynamic Ratings API, Dynamic Ratings Processor shall provide dynamic ratings for all transmission lines and autotransformers in less than 4 seconds. Dynamic Ratings Processor shall calculate and send real-time dynamic ratings to SCADA in less than 5 minutes. If Dynamic Ratings Processor fails to finish the processing of one cycle for a configurable amount of time, it shall be aborted and restarted automatically, with an alarm issued to the ERCOT operator. | Accepted | J. Dondeti | Protocols distinguish between Dynamic Ratings and the Dynamic Ratings Processor. So, we agree.
18 | Brazos Electric (T.Kroskey) | 17 | 4 | DR-SR2 |  | Description: The necessary software interfaces to EMS applications and data sources shall be modified to support the expected impacts to the Dynamic Ratings from other ERCOT components and from the Dynamic Ratings to other ERCOT systems components (including but not limited to Outage Evaluation, Transmission Constraint Manager, Real-time Contingency Analysis, State Estimator, Study Network Analysis, SCADA, and Alarm.). | Accepted | A. Boecker | Comment accepted as is.
19 | Brazos Electric (T.Kroskey) | 17 | 4 | DR-SR3 |  | … displays. | Accepted | A. Boecker | Editorial comment.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.