| OGRR Number | 204 | OGRR Title | Hotline Technology Update |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | November 13, 2007 |  |  |
| Operating Guide Section Requiring Revision |  | 8.3.3, QSE and TDSP Responsibilities (8.3.3 is also restated on Page 17 of the ERCOT Nodal ICCP Communications Handbook which should be updated concurrent with approval of this OGRR) |  |  |
| Proposed Effective Date |  | ## To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | Section 8.3.3 of the Operating Guides states that the “Hotline must be a 500 set not attached to the Market Participant’s Phone system.” Proposed language will allow continued use of either older, 500 set or any newer technology which operates independently from Market Participant’s commercial market communications (settlement) phone system. |  |  |
| ###### Overall Market Benefit |  | Increased reliability, expanded coordination ability and improved operator ease of use. |  |  |
| ###### Overall Market Impact |  | None. |  |  |
| ###### Consumer Impact |  | None. |  |  |
| ###### Procedural History |  | - On 9/20/07, this Operating Guides Revision Request (OGRR) was posted. - On 10/11/07, American Electric Power (AEP) comments were posted. - On 10/17/07, the Operations Working Group (OWG) considered this OGRR. - On 10/29/07, ERCOT comments were posted. - On 11/02/07, Luminant Energy comments were posted. - On 11/12/07, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 11/13/07, the OWG considered this OGRR. |  |  |
| ###### OWG Decision |  | On 10/17/07, the OWG tabled this OGRR. On 11/13/07, the OWG was in consensus to recommend approval of this OGRR as modified by the 11/12/07 OGRTF comments. |  |  |
| ###### Summary of OWG Discussion |  | On 10/17/07, the OWG was informed that ERCOT will submit comments on this OGRR. The OWG agreed to table this OGRR until it reviewed the ERCOT comments. On 11/13/07, the OWG reviewed the comments. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Market Participants would like the option to adopt new technologies with additional features, such as built-in redundancy. |  |
|  | 2 | New technologies with new features will continue to become available in the future and the proposed Operating Guides language allows Market Participants some flexibility to adopt some of these technologies as they become available. |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | Communications with ERCOT | None to slight savings |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Increased reliability | Difficult to quantify. |
|  | 2 | Expanded coordination ability | Difficult to quantify. |
|  | 3 | Improved operator ease of use | Difficult to quantify. |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Improved coordination and active redundant circuits will often have small, difficult to quantify financial benefits, but these features could occasionally become very valuable to the uninterrupted operation or rapid restoration of the bulk electric system during emergency conditions. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 | Section 8.3.3 of the Operating Guides mandates the use of a telephone technology which is no longer manufactured. Newer technologies are available, but not compliant with the Operating Guides as it is currently written. Proposed language maintains requirement of hotline operation to remain independent of the Market Participant’s commercial market communications (settlement) phone system, yet allows MP to select newer technologies at their option which include features such as built in redundancy. |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| AEP 101107 | Supported removing language that limits advancement into better and more secure phone communication technology. |
| ERCOT 102907 | Clarified language and elaborated. |
| Luminant Energy 110207 | Stated that a recommendation is not enforceable thus should not be included. |
| OGRTF 111207 | Clarified that the Hotline may be connected through the PBX system and that the Market Participant is responsible to reasonably assure continuous communication with ERCOT. |

| Original Sponsor |  |
| --- | --- |
| Name | Henry Durrwachter |
| E-mail Address | hdurrwachter@luminant.com |
| Company | Luminant Energy |

Proposed Operating Guide Language Revision

### 8.3.3	QSE and TDSP Responsibilities

TDSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TDSP.  Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

Any TDSP or QSE facility, whether primary or backup, involved in the transfer of the data sets identified in Attachment 8A, will be required to connect directly to the ERCOT WAN Frame Relay and Point-to-Point paths.  If a TDSP and QSE utilize the same EMS and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TDSP and QSE share a centralized Private Branch Exchange (PBX), separate Off Premise Extension (OPX) circuits will be terminated for each participant.

Each Market Participant is required to extend the ERCOT OPX and Hotline voice circuits into its system operations desk that is staffed continuously.  ERCOT will deliver the OPX and Hotline to a channel bank provided by the Market Participant.  The OPX and Hotline voice circuits are transported on separate Digital Signal Level 0 (DS0) channels.  In the event a Market Participant represents other entities through a QSE Letter of Agency, each entity represented must have dedicated OPX and Hotline circuits. It is the Market Participant’s responsibility to deliver the Hotline and the OPX to the Market Participant’s system operations desk in a manner that reasonably assures continuous communication with ERCOT and is not affected by PBX features such as automatic transfer or roll to voice mail.  The demarcation point for all voice circuits is the Market Participant’s channel bank.

A QSE or TDSP involved in the transfer of the critical data identified in Attachment 8A, will be required to provide the following communication resources to support the connection to the ERCOT private network:

- Private Network

  - Provide an analog business phone line or PBX analog extension for trouble shooting and maintenance of equipment.

  - Provide a height of 24” of rack space in a 19” wide rack.

  - Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above.

  - Provide building wiring from circuit termination to equipment rack.

  - Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility.

  - Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors.

  - Provide on site personnel to escort ERCOT employees or contractors.

  - Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT Local Area Network (LAN).

  - Market Participant will be required to sign a security connection agreement with ERCOT.

  - Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site.  Market Participants are responsible for their own security through this connection.

  - Provide a channel bank with at least one T1 interface, 4 Foreign Exchange Station (FXS) and two 4 wire analog ports.  Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment (e.g. Remote Terminal Unit (RTU)).  On the digital T1 stream, levels for voice are zero dpm for transmit and receive and levels for RTU are –13 dpm for transmit and receive.

  - Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended.

  - Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

- Internet (optional)

A QSE or TDSP not involved in the transfer of the data identified in Attachment 8A, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TDSP must then provide the above stated communications resources.