| PRR Number | 750 | PRR Title | Unannounced Generation Capacity Testing |
| --- | --- | --- | --- |
| Date |  | December 12, 2007 |  |
| Submitter’s Information |  |  |  |
| Name |  | Henry Durrwachter |  |
| E-mail Address |  | hdurrwachter@luminant.com |  |
| Company |  | Luminant Energy |  |
| Phone Number |  | 214-875-9285 |  |
| Cell Number |  | 214-437-4622 |  |
| Market Segment |  | IOU |  |

Comments

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Luminant Energy supports the concept of unannounced unit testing and offers the following comments which are designed to better explain and clarify the unannounced testing process and to address some circumstances that the original PRR did not identify.

Revised Proposed Protocol Language

6.10.2	General Capacity Testing Requirements

Within the first fifteen (15) days of the first day of each Season, each QSE shall provide ERCOT an HSL for any Generation Resource with a capacity greater than ten (10) MW that will be used to provide Ancillary Services during that Season.  ERCOT shall provide an appropriate form for QSEs to submit their HSL data.   The seasonal HSL shall take into account auxiliary Load and gross and net real power capability of the Generation Resource.  Each QSE shall update its Resource Plan and telemetry, as necessary, to reflect the seasonal HSL of each of its Generation Resources as well as other operational limitations.

To verify that the proper seasonal HSL is being reported, ERCOT may, at its discretion, conduct an unannounced seasonal Generation Resource test.   At a time determined solely by ERCOT, ERCOT will issue a Verbal Dispatch Instruction (VDI) to the QSE to operate the designated Generation Resource at its HSL as shown in the QSE’s current Resource Plan.  The QSE shall not be required to start the designated Generation Resource if it is not already on-line when ERCOT announces its intent to test the Resource.  If the designated Generation Resource is operating at its LSL when ERCOT sends the VDI to begin the test, the QSE shall have up to sixty (60) minutes to allow the Resource to reach 90% of its HSL and up to an additional twenty (20) minutes for the Resource to reach the HSL shown in the current Resource Plan.  This time requirement does not apply to nuclear-fueled Generation Resources.  Once the designated Generation Resource reaches its HSL, the QSE shall hold it at that output level for a minimum of thirty (30) minutes.  The HSL for the designated Generation Resource shall be determined based on the maximum MW produced by the Resource during the thirty (30) minutes of constant output.  After each test, QSEs will complete and submit an updated test form that ERCOT shall provide.

ERCOT may test multiple Generation Resources within a single QSE within a single twenty-four (24) hour period.  However, in no case, shall ERCOT test more than two Generation Resources within one QSE simultaneously.  ERCOT shall not perform an unannounced Generation Resource test during an Advisory, Alert or EECP event.  If an unannounced Generation Resource test is underway when an Advisory, Alert or EECP event commences, the test shall be cancelled.

Should the designated Generation Resource fail to reach its posted HSL within the time frame set forth herein, the maximum MW produced during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  The QSE shall have the opportunity to request another test at a time mutually agreed to by ERCOT and the QSE and may re-test as many times as desired.  The requested re-test shall take place within: the  first twenty-four (24) operating hours of the designated Generation Resource after the original test or three (3) Business Days after the original test.  In addition, the QSE may request, subject to ERCOT approval, a re-test at a time of its own choosing.  If such a test is approved by ERCOT, the QSE shall demonstrate the HSL of the designated unit for a period of at least sixty (60) minutes.  Any VDI ERCOT issues as a result of a QSE-requested re-test will not be compensated as an OOME payment under Protocol section 6.8.2.3 - Energy Payments but will be considered as an instructed deviation for compliance purposes.

If a Generation Resource designated for unannounced testing by ERCOT has posted a capacity de-rating in the Outage Scheduler, the test will measure the capability of the Resource to meet its de-rated capacity.  If the designated Generation Resource successfully meets the de-rated HSL, then no change shall be made to its rated HSL.  If the designated Generation Resource fails to meet the de-rated HSL, then its HSL will be revised to the maximum capacity demonstrated by the results of the unannounced test.  The QSE is then required to request a re-test (without compensation) of the designated Generation Resource to change its HSL to a higher level.

A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall evaluate the maximum capability of the Resource each Season.

ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) as it deems necessary at its sole discretion.  ERCOT shall report monthly the aggregated results of such unannounced testing (excluding re-tests), including, but not limited to, the number and total capacity of resources tested, the percentage of resources that met or exceeded their reported HSL, the percentage that failed to meet their reported HSL and the total MW capacity shortfall of those resources that failed to meet their reported HSL.

ERCOT shall conduct all unannounced Generation Resource testing by using OOME Dispatch Instructions to the Generation Resource under test.  Any re-testing the QSE requests shall be conducted at the QSE’s expense and shall not receive compensation through the normal ERCOT Settlement process.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement.

Specific Loads to be used for the first time as a Resource to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve must be correctly evaluated prior to their provisional qualification to provide Ancillary Services.  During the provisional qualification period, ERCOT shall conduct a qualification test of each LaaR consisting of an actual Load interruption.  If a LaaR passes the qualification test during the provisional qualification period, ERCOT shall consider the LaaR qualified to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve.  ERCOT shall develop a standard test procedure for the qualification test required under this subsection.

QSEs shall be responsible for qualifying any Load desiring to have the QSE represent it to provide Balancing Up Load (BUL) Service.

[PRR484: Add the following to the end of the above paragraph (“QSEs shall be responsible for qualifying…Balancing Up Load (BUL) Service. ”) upon system implementation:] Loads controlled under a qualified DLC program may be qualified as a group.

The QSE shall nominate to ERCOT, at least annually, that it is representing an amount of BUL for which it wishes to be qualified to provide.  At a time selected by ERCOT, the ERCOT operator will notify the QSE that it wants to verify the QSE’s ability to provide ERCOT with the appropriate signal simulating that it has initiated an ERCOT requested BUL reduction.  The QSE Operator will immediately simulate the initiation of the reduction and provide ERCOT with the appropriate signal representing some amount of Load to be qualified to provide BUL Resources.  Once ERCOT has verified that it has received an appropriate Load reduction signal from the QSE and has successfully completed the BUL registration process, the QSE will be qualified to provide BUL Resources.  Any changes to the BUL portfolio will require subsequent updates to the registration process.  For NOIEs representing specific Loads qualified as BULs that are located behind the NOIE Settlement Meter points, the NOIE shall provide an alternative unique descriptor of the qualified BUL Load for ERCOT’s records.

Generation Resources and Loads acting as Resources shall be evaluated at least annually by ERCOT for:

(1)	Correct operation of telemetry of the breakers controlling the Resource;

(2)	Correct mapping of QSE-provided telemetry of Ancillary Service energy to the appropriate energy Settlement Meter;

(3)	Data rate update requirements; and

(4)	Any other required telemetry attributes.

In addition, a LaaR that is used to provide Responsive Reserve Service will be subject to an actual interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected TDSP, at least once in every three hundred and sixty five (365) day period to verify ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, the LaaR must deploy at least 95% of its scheduled Load within ten (10) minutes of the receipt of the ERCOT Dispatch Instruction by the LaaR’s QSE.  If a LaaR has responded to an actual ERCOT Dispatch Instruction with at least a 95% reduction in its Load within ten (10) minutes in the applicable calendar year, ERCOT will use that response in lieu of another actual interruption test.  QSEs may request to have individual LaaRs aggregated for the purposes of actual interruption tests.  All performance evaluations will apply on an individual Resource basis.

All Generation Resources and Loads acting as a Resource shall meet all requirements specified in the Operating Guides for proper response to system frequency.  ERCOT may reduce the amount a Resource may contribute toward Ancillary Services if it finds unsatisfactory performance of the Resource as defined in these Protocols and the Operating Guides.

Qualification of a Resource, including a Load acting as a Resource or an EILS Resource, shall remain valid for such Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.