## Slide 1: ERCOT Wind Survey
Leo Villanueva

## Slide 2
Abilene
McCamey
Big Spring

## Slide 3
Far West

## Slide 4: Responses
Area | Number of surveys sent | Number of responses | Needs follow-up
Abilene | 15 | 15 | 5
Big Spring | 7 | 7 | 3
McCamey | 10 | 10 | 6
Far West | 2 | 2 | 0

## Slide 5: Abilene Area All the values are based on returned ERCOT survey results
Total number of Wind Powered Generation Resources (WPGR) 15 (15)
Total max rated capacity – 2271 MW
Average rated capacity – 151 MW
Average cut-off speed – 59 MPH
Average minimum wind speed at which generation starts – 8 MPH
Total rated reactive capability – 798 MVAr
Dynamic VAr control – 68% and Static VAr control – 32 %
Average number of turbines at each plant site – 98
37 % of the units in this area have feathering of the blades to control the output level

## Slide 6: Big Spring Area All the values are based on returned ERCOT survey results
Total number of WPGR’s 7 (7)
Total max rated capacity – 624 MW
Average rated capacity – 89 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 181 MVAr
Dynamic VAr control – 43% and Static VAr control – 57 %
Average number of turbines at each plant site – 80
26 % of the units in this area have feathering of the blades to control the output level

## Slide 7: McCamey Area All the values are based on ERCOT returned survey results
Total number of WPGR’s 10 (10)
Total max rated capacity – 761 MW
Average rated capacity – 76 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 290 MVAr
Dynamic VAr control – 20% , Static VAr control – 60 % and 20% non responsive.
Average number of turbines at each plant site – 154
20% the units have feathering of the blades to control the output level.

## Slide 8: Far West Area All the values are based on ERCOT returned survey results
Total number of WPGR’s 2 (2)
Total max rated capacity – 72 MW
Average rated capacity – 36 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 0 MVAr
Average number of turbines at each plant site – 71
None of the units have feathering of the blades to control the output level.

## Slide 9
Based on the survey results we have a total wind capacity of 3726 MW divided among 34 WPGR’s

## Slide 10
Region | Abilene (MVAr) | Big Spring (MVAr) | McCamey (MVAr)
Avg. Reactive Capability at 50% O/P | 33.14 | 10.788 | 17
Avg. Reactive Capability at 100% O/P | 49.25 | 15.775 | 29
Avg. Reactive Capability at no O/P | 9.05 | 6.029 | 0
Far west do not have any reactive capability

## Slide 11: What is the VAR Capability required in the Interconnection Agreement?
Abilene: 6 of 15 WPGR’s said 0.95 pf leading or lagging. 2 WPGR said 0.98 pf leading or lagging. 8 said none.
Big Spring: All the WPGR’s said 0.95 pf leading or lagging.
McCamey: 4 of 10 WPGR’s said 0.97 pf leading, 3 said 0.98 leading and 1 said 0.96 leading. 2 said none.
Far West: Both the WPGR’s said 1 pf leading or lagging.

## Slide 12: How far can units be backed down before operation becomes unstable?
Region | Abilene MW | Big Spring MW | McCamey MW
MW output per farm after which operation becomes unstable | 0.069 | 0.057 | 0
8 of 10 WPGR’s in McCamey and both WPGR’s in Far west said Curtailment is
achieved by stopping a group of turbines (groups are predetermined and
cycle through), not by reducing individual turbine output.

## Slide 13: Can individual turbines of this type be shut down at the facility on a routine basis (stop and start once per day)?
Abilene: 14 of 15 WPGR’s have the capability and 1 does not.
Big Spring: 7 of 7 WPGR’s have the capability of shutting individual turbines at the facility on a routine basis.
McCamey: 8 of 10 WPGR’s have the capability and 2 of 10 WPGR’s said that current control scheme does not shut down turbines but limit power output by modulating blade pitch.
Far West: Both WPGR’s have the capability.

## Slide 14: Are the facility turbines and control system and facility turbines able to provide automatic generation control (AGC) from a technical point of view? If not, would the turbines be capable of this if the control system was upgraded?
Abilene: 3 of 15 in Abilene area can provide AGC and 3 can provide with a control system upgrade.
Big Spring: 6 of 7 in Big Spring cannot provide automatic generation control (AGC). 1 can.
McCamey: Response was unclear.
Far West: None.

## Slide 15: How flexible is the zero output reactive capability? For example, is it manually or automatically switched in? What are the issues associated with provided this reactive capability if requested by ERCOT in Real Time.
Abilene: 3 of 15 have static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically. 3 cannot provide any flexibility. 4 said wind dependant. 3 said they are automatically controlled by two controllers, but that could take some programming work to implement. 1 said automatically controlled between +9 or -9 MVAr. 1 WPGR’s VAr output is attributed to the capacitive nature of the underground collection system. Capability is limited due to underground cable splices and thermal backfill material.
Big Spring Area: 5 of 7 do not have any flexible reactive capability at zero output. 1 has manual switching capability. 1 has static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically.
McCamey: None in McCamey area have flexible reactive capability at zero output.
Far West: None in this area have flexible reactive capability at zero output.

## Slide 16
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Abilene:
Under voltage - 299vac at the turbine. Over voltage - 365vac at the turbine. Over frequency - 61hz at the turbine. Under frequency - 59hz at the turbine. 25vac asymmetry between phases at the turbine for 6 of 15 WPGR’s
Voltage 110 % nominal or < 70 % nominal for 1 WPGR
No response from 8 WPGR’s

## Slide 17: What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Big Spring Area:
90% ≤ System Voltage ≥ 110% ; 94% ≤ System Frequency ≥ 104% is the response from 2 of 7 WPGR’s
High voltage 500V sensed phase to ground, low voltage 340V sensed phase to ground; For a V-47: high frequency 60.4hz, low frequency 59.2hz; For a V-66: high frequency 60.3hz, low frequency 59.5hz.
Over Freq>61Hz for 0.5 s, Under Freq <=59 Hz Over Vol>120% is the response from 2 WPGR’s
Response was unclear from 1 WPGR.

## Slide 18
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
McCamey:
Voltage 110 % nominal or < 70 % nominal for 2 of 10 WPGR’s
Response from 4 WPGR’s:
    85% V after 0.1 sec time delay (TD)
    90% V & 5 sec TD
    10% V & 60 sec TD
    112% V & 0.1 sec TD
Response from 4 WPGR’s:
    80% V & 0.2 sec TD
    90% V & 60 sec TD
    108% V & 5 sec TD
    110% V & 0.2 sec TD

## Slide 19
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Far west:
No response for this question.

## Slide 20: What is the response time required to reduce output by 20%? (time from ERCOT notice to reduce to time when wind-ranch is 20% below previous output)?
Average response time for 9 of 15 WPGR’s in Abilene is 8 min. 6 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output.”
Average response time for Big Spring is 24 min.
Average response time for 2 of 10 WPGR’s in McCamey is 10 min. 8 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.
2 of 2 WPGR’s in Far west have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.

## Slide 21: What is the response time required to increase output by 20% (presuming wind available)? (time from ERCOT notice to increased to time when wind-ranch is 20% above previous output?
Average response time for 9 of 15 WPGR’s in Abilene is 8 min. 6 have a response of “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output.”
Average response time for 5 of 7 WPGR’s Big Spring is 21 min.2 WPGR’s have a response of “This is not the way the system operates, the turbines are turned back on in groups to increase the maximum MW output - it does not "set" output.”
Average response time for 2 of 10 WPGR’s in McCamey is 10 min. 8 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.
2 of 2 WPGR’s in Far west have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output”.

## Slide 22: When turbines are being controlled what is the available ramping capability assuming wind conditions and system transmission conditions that could accommodate full output?
Abilene:
  6 of 15 WPGR’s response:
      0-100% (1,500kw per unit) less than 4 minutes
      75-100% (1,500kw) less than 1 minute
      50-75% (1,125kw) less than 1 minute
      25-50% (750kw) less than 1 minute
      0-25% (375kw) less than 1 minute
  2 WPGR’s response: There are no ramp rates. 0 – 100% output in 5 minutes (At perfect wind conditions)”.
  1 WPGR’s response: No ramp rates
  1 WPGR’s response:is “Individual turbine from 0 – 100 % in about 2.5 minutes. Entire farm in about 5 minutes (wind dependent).
Big Spring: Non responsive “There are no ramp rates”.
McCamey:
  2 of 10 WPGR’s response: “Individual turbine from 0 – 100 % in about 2.5 minutes. Entire farm in about 5 minutes (wind dependent).
  8 WPGR’s response: There are no ramp rates. 0 – 100% output in 5 minutes (At perfect wind conditions)”.
Far West: There are no ramp rates. 0 – 100% output in 5 minutes (At perfect wind conditions)”.