ERCOT Operations Report

December 2007 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration | Reason |
| --- | --- | --- | --- |
| 12/1 0:06:40 | 60.102 | 4 s | Out of DRS during schedule change. |
| 12/2 18:17:16 | 60.103 | 4 s | Server Failover. Steel Mill Load drop. |
| 12/5 10:45:57 | 59.864 | 6 s | 450 MW unit trip |
| 12/9 0:04:08 | 60.111 | 1 m 32 s | Out of DRS. Steel Mill Load drop. |
| 12/9 0:09:32 | 60.116 | 1 m 21 s | Out of DRS. Steel Mill Load drop. |
| 12/10 11:23:24 | 59.846 | 12 s | 565 MW unit trip |
| 12/12 1:48:30 | 59.791 | 3 m 8 s | Near DCS event. 2 unit trips totaling 1021 MW. |
| 12/12 1:58:18 | 60.161 | 6 m 7 s | LaaR Response |
| 12/14 7:54:36 | 59.878 | 42 s | 350 MW unit trip |
| 12/15 4:50:22 | 59.897 | 4 s | 265 MW DC Tie trip |
| 12/15 18:04:04 | 60.104 | 10 s | Balancing Error due to incorrect load forecast. |
| 12/19 8:51:38 | 59.828 | 1 m 6 s | 560 MW unit trip |
| 12/26 2:02:46 | 60.134 | 6 m 6 s | SCE corrected 800 MW. Out of DRS. |
| 12/27 5:47:02 | 60.109 | 2 m | Out of DRS. Wind Gen above schedule 400 MW. |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 12/3 23:19:50 | 12/3 23:26:28 | 0:06:38 | 315.46 | Out of Up Reg |
| 12/5 10:45:57 | 12/5 10:53:31 | 0:07:34 | 539.34 |  |
| 12/5 11:20:54 | 12/5 11:31:20 | 0:10:26 | 351.07 | Out of Up Reg |
| 12/6 6:03:14 | 12/6 6:12:12 | 0:08:58 | 315.46 | Schedule Change |
| 12/8 9:02:34 | 12/8 9:25:58 | 0:23:24 | 330.73 | 2 Units Trip |
| 12/8 18:04:30 | 12/8 18:11:10 | 0:06:40 | 320.54 | Unit Trip |
| 12/10 11:23:26 | 12/10 11:36:40 | 0:13:14 | 630.91 |  |
| 12/12 1:48:30 | 12/12 2:07:52 | 0:19:22 | 931.12 |  |
| 12/14 7:54:38 | 12/14 8:12:10 | 0:17:32 | 468.11 |  |
| 12/15 4:50:24 | 12/15 4:58:05 | 0:07:41 | 371.43 |  |
| 12/15 8:23:36 | 12/15 8:31:10 | 0:07:34 | 325.65 | SCE |
| 12/18 0:00:21 | 12/18 0:12:24 | 0:12:03 | 315.46 | Schedule Change |
| 12/19 8:51:36 | 12/19 9:07:50 | 0:16:14 | 722.51 |  |
| 12/21 21:03:16 | 12/21 21:23:26 | 0:20:10 | 310.37 | SCE |
| 12/22 4:45:20 | 12/22 4:58:56 | 0:13:36 | 320.54 | Deployments held due to RTB failure |
| 12/22 16:35:20 | 12/22 17:01:56 | 0:26:36 | 310.37 | SCE |
| 12/22 17:22:46 | 12/22 18:07:44 | 0:44:58 | 340.9 | WIND SCE |
| 12/22 21:26:14 | 12/22 21:41:16 | 0:15:02 | 325.65 | Unit Runback |
| 12/27 23:33:16 | 12/27 23:40:04 | 0:06:48 | 325.65 | Schedule Change |
| 12/30 23:00:00 | 12/30 23:10:08 | 0:10:08 | 320.54 | SCE |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 1 | 4 | 5 | 10 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 |
| DFW | 0 | 0 | 0 | 13 | 13 |
| E RIO | 0 | 1 | 2 | 0 | 3 |
| Houston | 0 | 0 | 0 | 8 | 8 |
| Laredo | 47 | 0 | 0 | 0 | 47 |
| North | 0 | 0 | 1 | 9 | 10 |
| Northeast | 0 | 0 | 0 | 2 | 2 |
| San Antonio | 0 | 0 | 0 | 3 | 3 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 39 | 0 | 0 | 39 |
| Western | 0 | 23 | 5 | 20 | 48 |
|  | 47 | 64 | 12 | 60 | 183 |

| Historical Totals | Dec-06 | Nov-07 | Dec-07 |
| --- | --- | --- | --- |
| Austin | 11 | 45 | 10 |
| Bryan Area | 0 | 1 | 0 |
| Corpus | 0 | 0 | 0 |
| DFW | 27 | 16 | 13 |
| E RIO | 5 | 10 | 3 |
| Houston | 1 | 44 | 8 |
| Laredo | 90 | 71 | 47 |
| North | 0 | 26 | 10 |
| Northeast | 0 | 1 | 2 |
| San Antonio | 1 | 18 | 3 |
| South | 0 | 0 | 0 |
| W RIO | 62 | 15 | 39 |
| Western | 0 | 17 | 48 |
| Total | 197 | 264 | 183 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Lorena - Waco West 69 kV | 5 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Robertson - Watson Chapel 138 kV | 5 |
| Martin Lake - Stryker Creek & Enterprise 345 kV | Elkton 345/138 kV Auto | 5 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Lake Creek - Temple Pecan Creek 138 kV | 4 |
| STP- Hillje & Whitepoint 345 kV | Blessing - Lolita 138 kV | 4 |
| Odessa EHV - Morgan Creek SES & Quail Switch 345 kV | Big Springs Switch - Big Springs West 138 kV | 4 |
| Menard - Gillespie 138 kV | Menard 138/69 kV Auto #1 | 4 |
| Fort Mason 138/69 kV Auto #1 | Menard 138/69 kV Auto #1 | 3 |
| Trinidad SES - Stryker Creek SES & Mt. Enterprise 345 kV | Athens - Athens North Switch 138 kV | 3 |
| Odessa EHV Switch 345/138 kV Auto #2 | Rexene Nylon Tap - Olefin Switch 138 kV | 3 |
| STP - Blessing 345 kV | Columbus - Stafford 69 kV | 3 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Sonora - Friess Ranch 69 kV | 3 |
| Baytown Energy Center - Chambers 345 kV | Baytown Auto #1 | 2 |
| Midland East - Odessa EHV 345 kV | Odessa Switch - Moss Switch 138 kV | 2 |
| Fisher Road - Oklaunion & Bowman 345 kV | Liberty REA - Lake Pauline 69 kV | 2 |
| STP - Hillje 345 kV | Blessing - Lolita 138 kV | 2 |
| STP - Whitepoint 345 kV | Blessing - Lane City 138 kV | 2 |
| Lytton Spring - Zorn & Austrop 345 kV | Turnersville - Goforth 138 kV | 2 |
| Austrop 345/138 kV Auto #1 | Austrop 345/138 kV Auto #2 | 2 |
| Sandow - Temple Switch 345 kV | Killeen Fort Hood West - Killeen Clark Road POI 138 kV | 2 |
| Comanche Peak - Decordova & Wolf Hollow - RockCreek 345 kV | Concord Auto | 1 |
| Decker - McNeil & Dessau - Daffin 138 kV | Garfield - Hicross 138 kV | 1 |
| Gillespie - Menard 138 kV | Gillespie - Phillips Mason 69 kV | 1 |
| Lon Hill - Nelson Sharpe 345 kV | Robstown city - City of Robstown 69 kV | 1 |
| Graham - Sweetwater Cogen & Graham - Long Creek 345 kV | Leon Switch - Putnam 138 kV | 1 |
| Cedar Bayou - Chambers & Northbelt 345 kV | Greens Bayou 345/138 kV Auto #1 | 1 |
| Midland East - Odessa EHV 345 kV | Odessa EHV - Rexene Nylon Tap 138 kV | 1 |
| Odessa EHV - Morgan Creek SES & Quail Switch 345 kV | Morgan Creek - Cal Energy 345 kV | 1 |
| Pawnee - Rayburn 138 kV | Rayburn 138/69 kV | 1 |
| South Channel - Jefferson 138 kV | Jefferson - Crown 138 kV | 1 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Waco West - Waco Woodway 138 kV | 1 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345 kV | Menard 138/69 kV Auto #1 | 1 |
| Lytton Springs - Zorn & Austrop 345 kV | Killeen Fort Hood West - Killeen Clark Road POI 138 kV | 1 |
| Blessing 345/138 kV Auto | Columbus - Stafford 69 kV | 1 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345 kV | Nacodoches 345/138 kV Auto | 1 |
| Fisher Road - Oklaunion & Bowman 345 kV | Abilene - Potosi Tap 138 kV | 1 |
| Hamilton - Sonora 138 kV | Campwood - Rocksprings 69 kV | 1 |
| Austrop - Lostpines 345 kV | Fayetteville - Winchester 138 kV | 1 |
| Dilley Switch - San Miguel Switch 138 kV | Derby - Pearsall 69 kV | 1 |
| West - North Stability limit |  | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North - West | 10 |
| West - North | 7 |

New RAP

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 12/21/2007 | Day Ahead Desk, V3 Rev35 | 356 |
| 12/20/2007 | Frequency Control Desk - V3R61 | 357 |
| 12/19/2007 | Shift Supervisor Desk, V3 Rev42 | 355 |
| 12/05/2007 | Frequency Control Desk - V3R60 | 354 |

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

12/6	13:30	Market System failed to send Ancillary Service awards to Market Participants.  Database issues.

12/11 	10:45 	Held Interval.  Oracle issues.

12/13	04:15 	Held Interval.  Oracle issues.

12/13 	18:15	Held Interval.  Oracle issues.

12/15 	05:30 	Held Interval.  Oracle issues.

12/22 	04:26 	Held Interval.  Market Clearing Engine issues.

12/31 	10:15 – 15:00	Ancillary Service Obligations re-published due to Responsive Reserve Obligation issues.

12/31 	13:00	Procurement of Ancillary Services extended to 1500 due to Texas Market Link (TML) issues.

12/31 	16:00 – 24:00  Day Ahead time line extended due to Replacement Reserve Service study failed to complete for 1/1/08.

1/1/08  00:00 – 02:00  Eight held consecutive intervals.

- Both issues related to zone changes.

Communication

None

## ERCOT peak (Unofficial)

12/17 	08:00  	43,975 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |
| --- | --- | --- | --- |
| MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
| 2006 | 2006 | 2007 |  |
| January | 4.79 | 4.55 |  |
| February | 4.81 | 3.75 |  |
| March | 4.95 | 2.70 |  |
| April | 5.59 | 3.00 |  |
| May | 3.59 | 3.22 |  |
| June | 2.65 | 4.46 |  |
| July | 2.62 | 4.29 |  |
| August | 2.09 | 3.11 |  |
| September | 4.03 | 3.78 |  |
| October | 3.63 | 3.08 |  |
| November | 3.28 | 2.95 |  |
| December | 3.44 | 3.74 |  |
| Annual Average | 3.79 | 3.55 |  |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event | Event |
| --- | --- | --- | --- | --- |
| 12/1 | 0:00 | 0:15 | Advisory | ARR below 3000 MW |
| 12/1 | 11:15 | 24:00 | Advisory | ARR below 3000 MW |
| 12/2 | 0:00 | 4:00 | Advisory | ARR below 3000 MW |
| 12/2 | 20:55 | 24:00 | Advisory | ARR below 3000 MW |
| 12/3 | 0:00 | 0:50 | Advisory | ARR below 3000 MW |
| 12/3 | 3:50 | 13:00 | Advisory | ARR below 3000 MW |
| 12/3 | 5:20 | 10:00 | Alert | ARR below 2500 MW. |
| 12/3 | 17:30 | 23:45 | Advisory | ARR below 3000 MW |
| 12/3 | 17:50 | 22:45 | Alert | ARR below 2500 MW. |
| 12/4 | 17:47 | 22:26 | Advisory | ARR below 3000 MW |
| 12/5 | 0:21 | 9:15 | Advisory | ARR below 3000 MW |
| 12/5 | 17:38 | 22:17 | Advisory | ARR below 3000 MW |
| 12/7 | 23:41 | 24:00 | Advisory | ARR below 3000 MW |
| 12/8 | 0:15 | 24:00 | Advisory | ARR below 3000 MW |
| 12/8 | 8:12 | 15:10 | Alert | ARR below 2500 MW. |
| 12/8 | 18:01 | 19:35 | Alert | ARR below 2500 MW. |
| 12/9 | 0:15 | 7:00 | Advisory | ARR below 3000 MW |
| 12/9 | 9:10 | 24:00 | Advisory | ARR below 3000 MW |
| 12/10 | 0:15 | 7:30 | Advisory | ARR below 3000 MW |
| 12/10 | 11:29 | 24;00 | Advisory | ARR below 3000 MW |
| 12/10 | 18:18 | 21:30 | Alert | ARR below 2500 MW. |
| 12/11 | 0:15 | 5:10 | Advisory | ARR below 3000 MW |
| 12/11 | 18:19 | 23:30 | Advisory | ARR below 3000 MW |
| 12/12 | 2:15 | 5:25 | Alert | ARR below 2500 MW. |
| 12/12 | 17:40 | 23:45 | Advisory | ARR below 3000 MW |
| 12/13 | 18:00 | 23:30 | Advisory | ARR below 3000 MW |
| 12/14 | 9:21 | 20:02 | Advisory | ARR below 3000 MW |
| 12/15 | 17:56 | 23:00 | Advisory | ARR below 3000 MW |
| 12/16 | 20:12 | 22:07 | Advisory | ARR below 3000 MW |
| 12/17 | 7:19 | 7:40 | Advisory | ARR below 3000 MW |
| 12/17 | 18:09 | 21:45 | Advisory | ARR below 3000 MW |
| 12/19 | 3:07 | 6:01 | Advisory | ARR below 3000 MW |
| 12/19 | 5:43 | 6:01 | Alert | ARR below 2500 MW. |
| 12/22 | 17:37 | 24:00 | Advisory | ARR below 3000 MW |
| 12/22 | 18:20 | 24:00 | Alert | ARR below 2500 MW. |
| 12/23 | 0:15 | 10:11 | Advisory | ARR below 3000 MW |
| 12/23 | 0:15 | 4:20 | Alert | ARR below 2500 MW. |
| 12/24 | 1:22 | 11:10 | Advisory | ARR below 3000 MW |
| 12/26 | 17:34 | 23:00 | Advisory | ARR below 3000 MW |
| 12/26 | 17:54 | 21:31 | Alert | ARR below 2500 MW. |
| 12/27 | 18:22 | 22:16 | Advisory | ARR below 3000 MW |
| 12/29 | 4:30 | 12:20 | Advisory | ARR below 3000 MW |
| 12/29 | 18:00 | 23:55 | Advisory | ARR below 3000 MW |

Transmission

12/10 11:40 – 12:35	Transmission Alert issued for loss of Military Highway - LaPalma 138 kV overloads Military Highway Transformer #2.

Other

12/12	 LaaR deployment due to 2 unit loss totaling 1021 MW.

12/23	Opened an Adjustment Period Replacement Reserve Market for hours 19:00-24:00.