| OGRR Number | 206 | OGRR Title | Black Start Satellite Phones |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | February 7, 2008 |  |  |
| Operating Guide Section Requiring Revision |  | 4.6.5, Emergency Back Up Communication Facilities Criteria. |  |  |
| Proposed Effective Date |  | ## March 1, 2008 |  |  |
| Priority and Rank Assigned |  | Not applicable |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) will require Transmission Service Providers (TSPs) that have contracted Black Start Resources or designated Black Start transmission corridors located within their transmission system to have a satellite phone as a backup communication system that is compatible with ERCOT’s satellite phone. |  |  |
| ###### Overall Market Benefit |  | This OGRR ensures that ERCOT and TSPs are able to communicate in Black Start conditions when alternative methods of communication may not be available and thus may improve reliability. |  |  |
| ###### Overall Market Impact |  | None. |  |  |
| ###### Consumer Impact |  | None. |  |  |
| ###### Procedural History |  | - On 10/18/07, this OGRR was posted. - On 11/12/07, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 11/13/07, the Operations Working Group (OWG) considered this OGRR. - On 12/05/07, the Impact Analysis (IA) was posted. - On 12/06/07, the ROS considered urgency for this OGRR. - On 12/12/07, the OWG considered the OWG Recommendation Report and IA for this OGRR. - On 01/10/08, ROS considered OGRR206. - On 2/7/08, TAC considered this OGRR. |  |  |
| ###### OWG Decision |  | On 11/13/07, the OWG was in consensus to recommend approval of this OGRR as modified by the 11/12/07 OGRTF comments. On 12/12/07, the OWG was in consensus to forward the Recommendation Report and the IA to the ROS for approval. |  |  |
| ###### Summary of OWG Discussion |  | On 11/13/07, the OWG reviewed the OGRTF comments. On 12/12/07, the OWG reviewed the IA. |  |  |
| ###### ROS Decision |  | On 12/06/07, the ROS unanimously voted to grant Urgent status to this OGRR. All Market Segments were present for the vote. On 01/10/08, ROS unanimously voted to recommend approval of this OGRR as recommended by OWG. All Market Segments were present for the vote. |  |  |
| ###### Summary of ROS Discussion |  | On 12/06/07, the OWG Chair explained that because the OWG meeting was moved from 12/14/07 to 12/13/07, the mandatory 21-day comment period requirement was not met. Unless this OGRR is granted Urgent status, the OWG will consider the OGRR language in December and the IA in January, thus delaying the OGRR by a month. The OWG Chair stated that in order to make the proposed revisions effective before the Black Start Resources are contracted, this OGRR needs to be granted Urgent status. On 01/10/08, there was no discussion. |  |  |
| ###### TAC Decision |  | On 2/7/08, TAC unanimously voted to approve OGRR206 as recommended by ROS. All Market Segments were present for the vote. |  |  |
| ###### Summary of TAC Discussion |  | On 2/7/08, a Market Participant expressed concerns that all Transmission Operators (TOs) will be required to have a satellite phone under this OGRR. Another Market Participant opined that having reliable communications will improve reliability thus the requirement to have a satellite phone is desirable. An on-going concern was raised that the definition of TO in the Operating Guides was not consistent with the North American Electric Reliability Corporation (NERC) definition. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Improved reliability and operations |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | N/A |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 | Operational readiness for potential Black Start event |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 111207 | Changed TSP to TO, removed the voice recording requirement and expanded the satellite phone requirement to all TOs. |

| Original Sponsor |  |
| --- | --- |
| Name | Dennis Starbuck on behalf of the Black Start Task Force |
| E-mail Address | Dennis.starbuck@austinenergy.com |
| Company | Austin Energy |

Proposed Operating Guide Language Revision

### 4.6.5	Emergency Back Up Communication Facilities Criteria

Reference:  Protocol Section 6.4.2, Determination of ERCOT Control Area Requirements (In Part)

…(7)	Black Start Service: ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required.  ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC policy.

(1)	All back up communications system shall meet the following minimum requirements:

- (a)	Be operational for seventy-two (72) hours immediately following the start of a blackout without external power from the ERCOT grid;

- (b)	Provide direct voice communications between:  Black Start Resource and TO; TOs and appropriate TOs; TOs and ERCOT;

- (c)	Have written procedures that address operator training and the testing of the communication system; and,

- (2)	TOs shall have a satellite phone that meets the minimum back up communication requirements as a back up communication system and that is compatible with ERCOT’s satellite phone.