| NPRR Number | 1xx | NPRR Title | Step-Up Transformer Reporting Requirements |
| --- | --- | --- | --- |
| Date |  | February xx, 2008 |  |
| Submitter’s Information |  |  |  |
| Name |  | Randy Jones |  |
| E-mail Address |  | rajones@calpine.com |  |
| Company |  | Calpine |  |
| Phone Number |  | (713) 830-8846 |  |
| Cell Number |  | (832) 385-3322 |  |
| Market Segment |  | Independent Generator |  |

Comments

| Overall Market Benefit | None |
| --- | --- |
| Overall Market Impact | Shifts Responsibility for Network Model Change control from TSPs to Resources. |
| Consumer Impact | None |

Calpine opposes the CenterPoint proposed changes to this NPRR.  The responsibility for providing this data to ERCOT should remain with the TSP since it is the TSP who dictates the necessary change to the no-load tap changer tap setting and the Resource is simply following the direction of the TSP.  The TSP “owns” the change and its impact to the models and the system and should therefore retain the responsibility of reporting it.

Additionally, of the reasons for this NPRR change Item #2 was chosen, while the proposed change clearly does change the intent of the original language as it applies to the reporting requirements.

Revised Proposed Protocol Language

3.10.7.1.4	Transmission and Generation Resource Step-Up Transformers

(1)	ERCOT shall model all transformers with a nominal low side (i.e., secondary, not tertiary) voltage above 60 kV.

(2)	ERCOT shall model all Generation Resource step-up transformers greater than ten MVA to provide for accurate representation of generator voltage control capability including the capability to accept a system operator entry of a specific no-Load tap position, or if changeable under Load, accept telemetry of the current tap position.

(3)	Each TSP and Resource Entity shall provide ERCOT with information to accurately describe each transformer in the Network Operations Model including any tertiary Load as required by ERCOT.  Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions Section 3.10.7.1, Modeling of Transmission Elements and Parameters:

(a)	Equipment owner(s);

(b)	Equipment operator(s);

(c)	The Transmission Element name;

(d)	The substation name;

(e)	Winding ratings;

(f)	Connectivity;

(g)	Transformer parameters, including all tap parameters; and

(h)	Other data necessary to model Transmission Element(s).

(4)	The Generation Entity shall provide parameters for each step-up transformer to ERCOT, which shall provide the information to TSPs.  Each TSP shall coordinate with the operators of the Resources connected to their respective systems to establish the proper transformer tap positions (no-Load taps).  The TSP shall report any changes to the transformer tap positions to ERCOT using the NOMCR process or other ERCOT prescribed means.  Each Generation Entity and each TSP shall schedule Generation Outages at mutually agreeable times to implement tap position changes when necessary.  If mutual agreement cannot be reached, then ERCOT shall decide where to set the tap position to be implemented by the Generation Entity at the next Generation Outage, considering expected impact on system security, future Outage plans, and participants. TSPs shall provide ERCOT and Market Participants with notice in accordance with 3.10.4, ERCOT Responsibilities, paragraph (4) (except for emergency) prior to the tap position change implementation date.

(5)	ERCOT shall post to the MIS Secure Area information regarding all transformers represented in the Network Operations Model.