## Slide 1: Texas Nodal Observability Status ROS Feedback Thursday, February 14, 2008

## Slide 2: EDS 2 – Early Delivery Systems
Unobservable Loads Monthly Update
  EDS 2 presented the following 3 options at the 11/08 ROS Meeting:
    TSPs provide Telemetry
    TSPs provide Calculated Points
    TSPs combine unobservable loads into a single load and provide
  ERCOT and TSPs agreed to Option 2 as the default option
    ERCOT will work with TSPs if they cannot comply with Option 2
Notes: <number>
<footer>
<header>
<date/time>

## Slide 3: Observability Status
Unobservable bus list issued to TSPs on November 19th 2007
9 TSPs out of 16 had unobservable busses with an action item
381 busses in total
First pass review uncovered model data issues with TSPs feedback and the list was reduced to 324 busses
Second pass review uncovered model data issues with TSPs feedback and the list was reduced to 245 busses
Unobservable bus list now down to 96 waiting on 3 TSPs
Issues:
  ERCOT is waiting for three TSPs to provide data so the model mapping issues can be complete.
  Additionally two TSPs have approximately 11 unobservable buses’ left between them that reside behind a third TSP’s network and can not complete their unobservable buses’ at this time.
Observations: link issues, polarity issues, ICCP data availability issues all affect the observability list.

## Slide 4: Observability Status-to-Date
Target date of February 14th 2008!

## Slide 5: Status-to-Date of QSE Points - Quality NOT Verified

## Slide 6: EDS 2 SE Improvement
EDS Environment has gained a small measure of stability with the new hardware.
  Fewer outages caused by software issues:
    Multiple Patch Releases in January 08
    Increased Zonal to Nodal database load compatibility
    Data limitations still exist
ICCP / SCADA Cleanup having a positive impact
  Generation approximately 98% in database
    Data Quality – Suspect but improving with ERCOT and MP join
    effort to find errors.
    ERCOT has designated a number of resources specifically to the
    collection, clean up and correction of missing, useless and
    incorrect data.
    Member participation and proactive attitude is greatly appreciated
    in this endeavor

## Slide 7: EDS 2 SE Improvement II
On January 25th the MW/Mvar Mismatch was set to 30 for Convergence
reporting to provide a more accurate view of the production environment.
Average convergence between Jan 15th and Feb 11th is 79.5.
Tolerance settings are bumped in the off-hours (night and weekend).
Off-hours Tolerance is set at the following
50 MW / 75 MVAR
Day time Tolerance is set at the following
30 MW / 30 MVAR

## Slide 8: State Estimator Convergence
Tolerance settings are bumped in the off-hours (night and weekend).
Off-hours Tolerance is set at the following
50 MW / 75 MVAR
Day time Tolerance is set at the following
30 MW / 30 MVAR

## Slide 9: EDS 2 – Next Steps
Next Steps
TSP’s provide data to ERCOT
  Telemetered Loads
  Calculated Loads
  Consolidated Loads (Model Loads)
ERCOT continuously runs observability report and provides feedback to TSPs
Service Request target of 2/14/2008 for Obervability if possible.
Service Request target of 2/21/2008 for Tap Estimation if possible.
Observations: link issues, polarity issues, ICCP data availability issues all affect the observability list.
Notes: <number>
<footer>
<header>
<date/time>