| OGRR Number | 198 | OGRR Title | Firm Load Shed Implementation Time Periods |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended for Approval |
| Date of Decision |  | February 6, 2008 |  |  |
| Operating Guide Section Requiring Revision |  | 4.5.3, Implementation |  |  |
| Protocol Section Requiring Revision, if any |  | ## None. |  |  |
| Proposed Effective Date |  | ## April 1, 2008 |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) adds language to the current ERCOT Operating Guides to provide maximum time periods allowed for firm Load shed implementation by Transmission and/or Distribution Service Providers (TDSPs) at the request of ERCOT System Operators when in Emergency Electric Curtailment Plan (EECP) Step 4. |  |  |
| ###### Overall Market Benefit |  | Provides guidance to ERCOT Compliance in monitoring TDSPs response to firm Load shed requests from ERCOT System Operators during EECP Step 4. |  |  |
| ###### Overall Market Impact |  | Unknown. |  |  |
| ###### Consumer Impact |  | Unknown. |  |  |
| ###### Procedural History |  | - On 05/09/07, OGRR198 was posted. - On 06/19/07, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 06/20/07, the Operations Working Group (OWG) considered the OGRR. - On 06/29/07, the Impact Analysis (IA) was posted. - On 07/18/07, the OWG considered the OWG Recommendation Report and the IA. - On 08/16/07, the ROS considered OGRR198. - On 09/06/07, the TAC considered this OGRR. - On 09/13/07, the ROS again considered this OGRR. - On 01/15/08, additional OGRTF comments were posted. - On 02/01/08, the Operations Working Group (OWG) considered this OGRR via email. |  |  |
| ###### OWG Decision |  | On 06/20/07, the OWG was in consensus to recommend approval of OGRR198 as submitted. On 07/18/07, the OWG was in consensus to forward the OWG Recommendation Report and the IA to ROS for approval. On 02/01/08, the OWG was in consensus via email to forward OGRR198 as revised by 011508 OGRTF comments to ROS for approval. |  |  |
| ###### Summary of OWG Discussion |  | On 06/20/07, there was no discussion. On 07/18/07, there was no discussion. On 02/01/08, there was no discussion. |  |  |
| ###### ROS Decision |  | On 08/16/07, the ROS recommended approval of OGRR198 as recommended by the OWG. There was one opposing vote from the Electric Cooperative Market Segment. All Market Segments were present for the vote. On 09/13/07, the ROS was in consensus to refer this OGRR to an ad hoc task force to be led by Henry Wood. |  |  |
| ###### Summary of ROS Discussion |  | On 08/16/07, there was no discussion. On 09/13/07, a Market Participant (MP) opined that the term “avoidable delay” is too vague and suggested that it is possible to shed firm Load within 10-15 minutes via SCADA systems as is done to comply with the Disturbance Control Standard (DCS) noting that most Load is controlled by a SCADA system versus remote switching which requires manual intervention. The MP suggested that Operators should be provided complete authority when in EECP Step 4 and should act as soon as possible regardless of the deadline as EECP Step 4 is the last step before possible blackouts. Participants argued that some MPs may not have the systems and resources to meet more stringent timelines. ERCOT staff stated their expectation that TDSPs would act without delay and that the timelines were only provided for compliance purposes. The ROS Chair suggested that Load shed practices, type of Loads to be shed, criteria, order and timing should be discussed further and the ROS was in consensus to constitute an ad hoc task force. |  |  |
| ###### TAC Decision |  | On 09/06/07, the TAC unanimously remanded this OGRR to the ROS to review the proposed firm Load shed timelines. All Market Segments were present for the vote. |  |  |
| ###### Summary of TAC Discussion |  | On 09/06/07, a Market Participant opined that a 30-minute delay in shedding Load may result in a black-out and that with today’s technology Load shed timelines could be reduced. Participants inquired whether the ROS discussed the timelines and was informed that while the OWG did, the ROS did not discuss this issue in detail. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Firm load shed requests from ERCOT are initiated when in EECP Step 4. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | TDSPs | N/A |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | ERCOT Compliance | N/A |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | John Jonte |
| E-mail Address | john.jonte@CenterPointEnergy.com |
| Company | CenterPoint Energy |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 061907 | Recommended approval of OGRR198 as submitted. |
| OGRTF 011508 | Proposed language to identify the immediate need for firm Load shed when requested by ERCOT and that the responsible Entity for firm Load shed is the Transmission Service Provider (TSP), or the designated agent. |

Proposed Operating Guide Language Revision

### 4.5.3	Implementation

ERCOT shall be responsible for monitoring system conditions, initiating the EECP steps below, notifying all QSEs and TOs, and coordinating the implementation of the EECP Conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each ERCOT declared EECP Step.

ERCOT has the authority to obtain Emergency Assistance energy over the DC tie(s) for use by ERCOT.  ERCOT is also the coordinating authority for requests for emergency type power into or out of ERCOT.

ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

There may be insufficient time to implement all steps in sequence.  ERCOT can immediately implement Step 4 of the EECP any time the system frequency is below 59.8 Hz and will immediately implement Step 4 any time the frequency is below 59.5 Hz.

Percentages for Step 4 Load shedding will be based on the previous year's TDSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

The ERCOT System Operator shall declare the EECP steps to be taken by QSEs and TDSPs.  QSEs and TDSPs shall implement actions under that Step (and all above if not previously accomplished) and if ordered by the ERCOT Shift Supervisor or his designate, shall report back to the ERCOT System Operator when the requested step has been completed.

During EECP Step 4, ERCOT must be capable of shedding sufficient firm load to arrest frequency decay and to prevent generator tripping.  The amount of firm load to be shed may vary depending on ERCOT grid conditions during the event. Each TSP will be capable of shedding their allocation of firm load, without delay.  The maximum time for the TSP to interrupt firm load will depend on how much load is to be shed and whether the load is to be interrupted by SCADA or by the dispatch of personnel to substations.  Since the need for firm load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed thirty (30) minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed load will be implemented within a time period not to exceed one (1) hour;

(c)	The initial clock on the firm load shed shall apply only to load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first load shed instruction, ERCOT determines that an additional amount of firm load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

Each TSP, or its Designated Agent, will provide ERCOT a status report of load shed progress within thirty (30) minutes of the time of ERCOT’s instruction or upon ERCOT’s request.