ERCOT Operations Report

January 2008 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration | Reason |
| --- | --- | --- | --- |
| 1/7/2008 0:05 | 60.117 | 02:41 | Out of DRS. SCE change 250 MW. Steel Mill load drop 100 MW. |
| 1/7/2008 22:01 | 60.147 | 08:15 | 4240 MW Schedule Change. QSE SCE up to 681 MW due to units not ramping down for 10 minutes. |
| 1/8/2008 22:05 | 59.893 | 00:04 | 2510 MW Schedule Change |
| 1/12/2008 18:20 | 60.112 | 00:38 | 250 MW SCE change. 150 MW Steel mill Load drop. |
| 1/13/2008 18:04 | 60.109 | 00:06 | Bad offset. |
| 1/20/2008 3:36 | 59.89 | 00:02 | 370 MW Unit Trip. |
| 1/22/2008 6:13 | 59.895 | 00:04 | Multiple unit trips totaling 400 MW. |
| 1/22/2008 8:23 | 59.896 | 00:02 | 250 MW unit trip. |
| 1/31/2008 3:19 | 60.114 | 01:52 | Out of DRS. Wind SCE out 800 MW. |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/1 2:01:14 | 1/1 2:29:12 | 0:27:58 | 335.82 | 8 Held Intervals |
| 1/3 5:55:54 | 1/3 6:00:14 | 0:04:20 | 310.37 | SCE & Schedule Change |
| 1/3 8:13:34 | 1/3 8:27:48 | 0:14:14 | 356.16 | Unit Trips |
| 1/4 22:01:01 | 1/4 22:07:24 | 0:06:23 | 329.04 | Out of URS. SCE Change Schedule Change |
| 1/5 0:29:42 | 1/5 0:36:58 | 0:07:16 | 315.46 | SCE & Recalling DRS. |
| 1/7 19:34:14 | 1/7 19:44:14 | 0:10:00 | 320.54 | SCE & Recalling DRS. |
| 1/7 23:33:12 | 1/7 23:38:24 | 0:05:12 | 340.9 | SCE & Recalling DRS. |
| 1/8 22:05:10 | 1/8 22:10:34 | 0:05:24 | 401.01 |  |
| 1/8 23:18:02 | 1/8 23:22:02 | 0:04:00 | 317.69 | Unit Trip |
| 1/8 23:34:38 | 1/8 23:44:14 | 0:09:36 | 322.9 | Out of URS |
| 1/9 0:05:22 | 1/9 0:11:54 | 0:06:32 | 359.35 | SCE |
| 1/9 3:49:54 | 1/9 3:59:18 | 0:09:24 | 328.1 | DC Tie curtailment due to TLR |
| 1/15 21:21:06 | 1/15 21:42:14 | 0:21:08 | 322.9 | Out of URS & SCE |
| 1/20 3:36:14 | 1/20 3:43:58 | 0:07:44 | 416.65 |  |
| 1/20 6:04:18 | 1/20 6:12:22 | 0:08:04 | 317.69 | Schedule Change, Wind OOM down, & Steel Mill Load Pickup |
| 1/20 19:20:21 | 1/20 19:28:26 | 0:08:05 | 322.9 | Wind drop, System Load pickup |
| 1/21 10:32:04 | 1/21 10:46:10 | 0:14:06 | 343.74 | QSE Loss of SCADA. Out of URS. |
| 1/22 6:13:52 | 1/22 6:16:56 | 0:03:04 | 390.6 |  |
| 1/22 8:23:54 | 1/22 8:30:26 | 0:06:32 | 385.4 |  |
| 1/22 23:44:01 | 1/22 23:53:42 | 0:09:41 | 338.53 | Steel Mill Load Pickup |
| 1/26 0:29:28 | 1/26 0:33:18 | 0:03:50 | 348.94 | Unit Trips |
| 1/27 0:33:52 | 1/27 0:51:08 | 0:17:16 | 359.35 | Steel Mill & System Load Pickup |
| 1/30 22:02:30 | 1/30 22:09:34 | 0:07:04 | 317.69 | Schedule Change |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 1 | 0 | 2 | 3 |
| Bryan Area | 0 | 3 | 4 | 0 | 7 |
| Corpus | 0 | 0 | 0 | 0 | 0 |
| DFW | 0 | 1 | 0 | 3 | 4 |
| E RIO | 0 | 0 | 0 | 0 | 0 |
| Houston | 0 | 0 | 0 | 1 | 1 |
| Laredo | 51 | 0 | 0 | 0 | 51 |
| North | 0 | 0 | 1 | 4 | 5 |
| Northeast | 0 | 2 | 0 | 7 | 9 |
| San Antonio | 0 | 0 | 1 | 1 | 2 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 |
| Western | 0 | 4 | 0 | 12 | 16 |
|  | 51 | 11 | 6 | 30 | 98 |

| Historical Totals | Jan-07 | Dec-07 | Jan-08 |
| --- | --- | --- | --- |
| Austin | 83 | 10 | 3 |
| Bryan Area | 0 | 0 | 7 |
| Corpus | 6 | 0 | 0 |
| DFW | 54 | 13 | 4 |
| E RIO | 39 | 3 | 0 |
| Houston | 21 | 8 | 1 |
| Laredo | 91 | 47 | 51 |
| North | 13 | 10 | 5 |
| Northeast | 12 | 2 | 9 |
| San Antonio | 24 | 3 | 2 |
| South | 30 | 0 | 0 |
| W RIO | 81 | 39 | 0 |
| Western | 20 | 48 | 16 |
| Total | 474 | 183 | 98 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple Switch - Killeen Switch & Sandow Switch 345kV | Killeen Switch - Harker Heights South | 7 |
| Odessa EHV - Morgan Creek SES - Quail Switch 345kV | Morgan Creek SES - Cal Energy 345kV | 6 |
| Spur 138/69kV Auto #1 | Spur - Girard Tap 69kV | 6 |
| San Angelo Red Creek 345/138kV Auto #1 | San Angelo Red Creek 345/138kV Auto #2 | 5 |
| Temple Switch - Killeen Switch & Sandow Switch 345kV | Belton - Belton Southwest 138kV | 4 |
| Ballinger - Santa Anna 138kV | Ballinger - Humble Ballinger 69kV | 2 |
| Bosque Switch - Whitney 138kV | Whitney - Lake Whitney 138kV | 2 |
| Fort Mason 138/69kV autotransformer | Menard 138/69kV Auto #1 | 2 |
| San Miguel Switch - Dilley Switch 138kV | Derby - Pearsall 69kV | 2 |
| Trinidad SES - Stryker Creek SES & Mt Enterprise 345kV | Athens Tap - Athens North Switch 138kV | 2 |
| Trinidad SES - Stryker Creek SES & Stryker Creek SES - Mt. Enterprise 345kV | Athens Tap - Athens North Switch 138kV | 2 |
| Twin Buttes - San Angelo 345kV | Twin Buttes Auto #1 | 2 |
| Graham - Sweetwater Cogen & Graham - Long Creek | Abilene South - Potosi Tap | 2 |
| Austrop 345/138kV auto #2 | Austrop 345/138kV Auto #1 | 1 |
| Austrop - Lost Pines 345kV | Fayetteville - Winchester 138kV | 1 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345kV | Nacogdoches SE - Herty North Switch 138kV | 1 |
| Fisher Road - Oklaunion & Fisher - Bowman 345kV | Abilene South - Potosi Tap 138kV | 1 |
| Graham - Sweetwater - Long Creek 345kV | Abilene South - Potosi Tap 138kV | 1 |
| Lytton Springs - Austrop - Zorn 345kV | Canyon-Rohr 138kV | 1 |
| Menard - Gillespie 138kV | Menard 138/69kV Auto #1 | 1 |
| Menard - Gillespie 138kV | Gillespie LCRA - Phillips Mason Tap 69kV | 1 |
| Mount Enterprise - Trinidad & Stryker Creek - Martin Lake 345kV | Nacogdoches 345/138kV Auto #1 | 1 |
| West – North Stability |  | 4 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North-West | 9 |
| North-South | 8 |
| West-North | 7 |
| South-North | 5 |

New RAP

None

New Procedures/Forms/Operations Bulletins

None

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

1/18 – 1/20	RPRS failure to meet Day-Ahead time-line.  Code migration caused a delay in a separate function.

1/20  	Held 18:45 Interval due to an incorrect value entered in for the OC1 adjustment constraint tool.

Communication

None

## ERCOT peak (Unofficial)

01/03 	08:00  	45,337 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | NA |
| March | 3.41 | 4.95 | 2.70 | NA |
| April | 3.37 | 5.59 | 3.00 | NA |
| May | 4.21 | 3.59 | 3.22 | NA |
| June | 3.91 | 2.65 | 4.46 | NA |
| July | 5.22 | 2.62 | 4.29 | NA |
| August | 4.86 | 2.09 | 3.11 | NA |
| September | 6.24 | 4.03 | 3.78 | NA |
| October | 4.51 | 3.63 | 3.08 | NA |
| November | 4.53 | 3.28 | 2.95 | NA |
| December | 5.95 | 3.44 | 3.74 | NA |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.30 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event | Event |
| --- | --- | --- | --- | --- |
| 1/2/08 | 18:55 | 21:30 | Advisory | ARR below 3000 MW |
| 1/11/08 | 7:02 | 8:03 | Advisory | ARR below 3000 MW |
| 1/20/08 | 5:10 | 10:15 | Advisory | ARR below 3000 MW |
| 1/26/08 | 23:01 | 24:00 | Advisory | ARR below 3000 MW |
| 1/27/08 | 0:15 | 7:30 | Advisory | ARR below 3000 MW |
| 1/31/08 | 19:47 | 24:00 | Advisory | ARR below 3000 MW |

Other

1/04 	13:36	Matador SPS armed and actuated

1/09	15:45	Monticello Mining SPS armed and actuated

1/15	17:04	McDonald Road SPS armed and actuated

1/21	07:14	McDonald Road SPS armed and actuated

1/21	10:04	Matador SPS armed and actuated

1/22	06:13	Simultaneous loss of 345 kV line and 5 wind units

1/23 	19:45	Matador SPS armed and actuated

1/26	04:57	Matador SPS armed and actuated

1/29	13:55	Four 345 kV lines and one 345/138 kV autotransformer tripped in the

West Zone.  TO reported range fire in the area.