| PRR Number | 750 | PRR Title | Unannounced Generation Capacity Testing |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | February 19 2008 |  |  |
| Protocol Section Requiring Revision |  | 6.10.2, General Capacity Testing Requirements |  |  |
| Effective Date |  | March 1, 2008 |  |  |
| Priority and Rank Assigned |  | n/a |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) replaces the seasonal testing requirement with unannounced Generation Resource testing and adds a requirement for Qualified Scheduling Entities (QSEs) to seasonally update their Resources’ High Sustainable Limits (HSLs). |  |  |
| Overall Market Benefit |  | Improved accuracy in reserve reporting. |  |  |
| Overall Market Impact |  | Possibility of increased Out of Merit Energy (OOME) cost. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Credit Impacts |  | TBD |  |  |
| Procedural History |  | - PRR750 and its Impact Analysis (IA) were posted on 12/11/07. - On 12/12/07, Exelon, Luminant, and the City of Dallas comments were posted. - On 12/13/07, FPL Energy (FPLE) and Luminant comments were posted. - On 12/13/07, PRR750 was granted Urgent status by e-mail vote. - On 1/8/08, LCRA comments were posted. - On 1/11/08, Exelon comments were posted. - On 1/16/08, FPLE, CPS Energy, Calpine, NRG Texas, and PUC Staff comments were posted. - On 1/17/08, PRS considered PRR750. - On 2/4/08, FPLE’s second set of comments were posted. - On 2/6/08, ERCOT Staff comments were posted. - On 2/7/08, FPLE’s third set of comments were posted. - On 2/7/08, TAC considered this PRR. - On 2/19/08, the ERCOT Board of Directors (Board) considered PRR750. |  |  |
| PRS Decision |  | On 1/17/08, PRS voted to recommend approval of PRR750 as modified at PRS based on comments by and discussions with Luminant, LCRA, PRS and ERCOT Staff. The motion passed with one abstention from the Municipally Owned Utility (MOU) Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 1/17/08, participants discussed the timing of the tests; responsible party for the cost of the test; the testing timelines; the role of the HSL and Low Sustainable Limit (LSL); the impact of the reasonability numbers on the tests and other measures in the Resource Plans; impacts of the tests on the Reserve Discount Factor (RDF); the method of calculation of the integrated megawatt (averaged over 30 minutes; testing methodology for Combined Cycle units); and management of emergencies and Alerts during testing. Some participants expressed concerns related primarily to the relationship between the HSL and the reasonability numbers in the test, and how this may create stranded capacity. Participants noted that Load will contribute a percentage of the cost of these testing obligations and that this will ultimately increase costs for Load. PRS revised the PRR based on discussion of comments submitted by Exelon, Luminant, City of Dallas, FPL Energy, LCRA, CPS Energy, Calpine, NRG Texas, and PUC Staff. |  |  |
| TAC Decision |  | On 2/7/08, TAC voted to recommend approval of PRR750 as recommended by PRS and as revised by TAC. The motion passed with one abstention from the Independent Power Marketer Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 2/7/08, Generators objected to having a link between the HSL and the ramp rate, and argued that this PRR creates a new definition for HSL. Generators commented that this PRR may not give ERCOT the tools to determine actual capacity availability. ERCOT Staff and other participants responded that this PRR is the product of three months of negotiations and represents a compromise. ERCOT Staff objected to the proposal to eliminate the implied ramp rate provisions. Participants emphasized that the purpose of this PRR is to show ERCOT and the Reliability and Operations Subcommittee (ROS) the actual capability of a Generation unit, and move to remove the Discount Factor. Some participants opined that this PRR may not be ripe for consideration. The Independent Market Monitor (IMM) concurred with the objections of ERCOT Staff related to the proposal to eliminate the implied ramp rate provisions and urged the TAC to move the PRR forward without those particular proposed changes. Proponents of PRR750 urged consideration of this PRR at this meeting and suggested that late comments could be incorporated in a subsequent PRR. Participants also clarified language related to settlements. |  |  |
| Board Decision |  | On 2/19/08, the Board approved PRR750 as revised by the Board. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 |  | Could increase OOME uplift. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Improved accuracy in reserve reporting. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Exelon 121207 | Urged against granting Urgent status to allow for more time to vet the issues. |
| Luminant 121207 | Supported the premise of the PRR and offered suggestions for unannounced testing procedures. |
| City of Dallas 121207 | Supported the concept of enhanced and unannounced testing of resources and offered revisions to refine and clarify the testing process. |
| FPLE 121307 | Urged delay in granting Urgent status to this PRR until such time as the language can be revised to address unanswered questions and expressed support of the comments submitted by Exelon. |
| Luminant 121307 | Revised its comments dated December 12, 2007 based on discussions and agreements reached by the PRR750 Task Force. |
| LCRA 010808 | Offered clarifying revisions and submitted questions. |
| Exelon 011108 | Commented that the proposed changes to the Resource Plan HSLs are at odds with the Resource Plan Metrics in Section 4.10.4. |
| FPLE 011608 | Suggested removing the binding Seasonal HSL limit. |
| CPS Energy 011608 | Proposed that if a Resource meets its stated HSL from the Resource Plan, the Resource should be allowed to keep the HSL value stated at the beginning of the Season. |
| Calpine 011608 | Commented that unannounced testing, if not structured properly, can be a significant burden on not only large fleet owners, but also the ISO. Supported changes proposed by Luminant and Exelon. |
| NRG Texas 011608 | Commented that the PRR could have unintended consequences of removing capacity from the market, reducing the accuracy of HSLs and suppressing market prices. |
| PUC Staff 011608 | Supported unannounced testing as a means to mitigate or eliminate the need for a RDF and provide ERCOT with accurate capacity data. |
| FPLE 020408 | Proposed eliminating the implied ramp rate provisions and offered clarifying language regarding the terminology related to the HSL. |
| ERCOT 020608 | Objected to the proposal to eliminate the implied ramp rate and recommended rejecting FPLE’s comments. |
| FPLE 020708 | Proposed eliminating the implied ramp rate provisions in additional section of the PRR and offered additional clarifying language. |

| Original Sponsor |  |
| --- | --- |
| Name | John Dumas |
| Company | ERCOT |
| Market Segment | n/a |

Proposed Protocol Language Revision

6.10.2	General Capacity Testing Requirements

Within the first fifteen (15) days of each Season, each QSE shall provide ERCOT a seasonal HSL for any Generation Resource with a capacity greater than ten (10) MW that will be operated  during that Season.  ERCOT shall provide an appropriate form for QSEs to submit their seasonal HSL data.   The seasonal HSL shall take into account auxiliary Load and gross and net real power capability of the Generation Resource.  Each QSE shall update its Resource Plan and telemetry, as necessary, to reflect the HSL of each of its Generation Resources in a given operating interval as well as other operational limitations.

To verify that the   HSL reported in the Resource Plan is achievable, ERCOT may, at its discretion, conduct an unannounced Generation Resource test.   At a time determined solely by ERCOT, ERCOT will issue a Verbal Dispatch Instruction (VDI) to the QSE to operate the designated Generation Resource at its HSL as shown in the QSE’s Resource Plan at the time the test is initiated.  The QSE shall not be required to start the designated Generation Resource if it is not already on-line when ERCOT announces its intent to test the Resource.  If the designated Generation Resource is operating at its LSL when ERCOT sends the VDI to begin the test, the QSE shall have up to  sixty (60) minutes to allow the Resource to reach 90% of its HSL and up to an additional twenty (20) minutes for the Resource to reach the HSL shown in the Resource Plan at the time the test is initiated.  This time requirement does not apply to nuclear-fueled Generation Resources.  If the designated Generation Resource is operating between its LSL and 50% of its HSL when ERCOT begins the test, the QSE shall have sixty (60) minutes for the Resource to reach its HSL.  If the Resource is operating at or above 50% of its HSL when ERCOT begins the test, the QSE shall have thirty (30) minutes for the Resource to reach its HSL.  Once the designated Generation Resource reaches its HSL, the QSE shall hold it at that output level for a minimum of thirty (30) minutes.  The HSL for the designated Generation Resource shall be determined based on the real-time averaged MW telemetered by the Resource during the thirty (30) minutes of constant output.  After each test, QSEs will complete and submit an updated test form that ERCOT shall provide.

ERCOT may test multiple Generation Resources within a single QSE within a single twenty-four (24) hour period.  However, in no case, shall ERCOT test more than two Generation Resources within one QSE simultaneously.  All Resources On-line in an Aggregated Unit will be measured on an aggregate capacity basis.  All QSEs associated with a jointly owned unit will be tested simultaneously.  Hydro and wind generation will be excluded from unannounced generation capacity testing.  ERCOT shall not perform an unannounced Generation Resource test during an Alert or EECP event.  If an unannounced Generation Resource test is underway when an Alert or EECP event commences, ERCOT may cancel the test .

Should the designated Generation Resource fail to reach its  HSL as posted in its Resource Plan within the time frame set forth herein, the real-time averaged MW telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  The QSE shall have the opportunity to request another test at a time determined by ERCOT and may retest as many times as desired.  Subject to ERCOT approval, the requested retest will take place within: the  first twenty-four (24) operating hours of the designated Generation Resource after the request for retest or three (3) Business Days after the request for retest.  Any VDI ERCOT issues as a result of a QSE-requested retest will not be compensated under Protocol section 6.8.2.3, - Energy Payments, but will be considered as an instructed deviation for compliance purposes.

A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall evaluate the maximum capability of the Resource each Season.

ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of appropriate TAC subcommittee.  ERCOT shall report monthly the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of resources tested, the percentage of resources that met or exceeded their HSL reported in the Resource Plan, the percentage that failed to meet their HSL reported in the Resource Plan and the total MW capacity shortfall of those resources that failed to meet their HSL reported in the Resource Plan.

ERCOT shall conduct all unannounced Generation Resource testing by using OOME Dispatch Instructions to the Generation Resource under test.  Any VDI ERCOT issues as a result of a QSE-requested retest will not be compensated under Protocol section 6.8.2.3, - Energy Payments, but will be considered as an instructed deviation for compliance purposes.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement.

Specific Loads to be used for the first time as a Resource to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve must be correctly evaluated prior to their provisional qualification to provide Ancillary Services.  During the provisional qualification period, ERCOT shall conduct a qualification test of each LaaR consisting of an actual Load interruption.  If a LaaR passes the qualification test during the provisional qualification period, ERCOT shall consider the LaaR qualified to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve.  ERCOT shall develop a standard test procedure for the qualification test required under this subsection.

QSEs shall be responsible for qualifying any Load desiring to have the QSE represent it to provide Balancing Up Load (BUL) Service.

[PRR484: Add the following to the end of the above paragraph (“QSEs shall be responsible for qualifying…Balancing Up Load (BUL) Service. ”) upon system implementation:] Loads controlled under a qualified DLC program may be qualified as a group.

The QSE shall nominate to ERCOT, at least annually, that it is representing an amount of BUL for which it wishes to be qualified to provide.  At a time selected by ERCOT, the ERCOT operator will notify the QSE that it wants to verify the QSE’s ability to provide ERCOT with the appropriate signal simulating that it has initiated an ERCOT requested BUL reduction.  The QSE Operator will immediately simulate the initiation of the reduction and provide ERCOT with the appropriate signal representing some amount of Load to be qualified to provide BUL Resources.  Once ERCOT has verified that it has received an appropriate Load reduction signal from the QSE and has successfully completed the BUL registration process, the QSE will be qualified to provide BUL Resources.  Any changes to the BUL portfolio will require subsequent updates to the registration process.  For NOIEs representing specific Loads qualified as BULs that are located behind the NOIE Settlement Meter points, the NOIE shall provide an alternative unique descriptor of the qualified BUL Load for ERCOT’s records.

Generation Resources and Loads acting as Resources shall be evaluated at least annually by ERCOT for:

(1)	Correct operation of telemetry of the breakers controlling the Resource;

(2)	Correct mapping of QSE-provided telemetry of Ancillary Service energy to the appropriate energy Settlement Meter;

(3)	Data rate update requirements; and

(4)	Any other required telemetry attributes.

In addition, a LaaR that is used to provide Responsive Reserve Service will be subject to an actual interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected TDSP, at least once in every three hundred and sixty five (365) day period to verify ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, the LaaR must deploy at least 95% of its scheduled Load within ten (10) minutes of the receipt of the ERCOT Dispatch Instruction by the LaaR’s QSE.  If a LaaR has responded to an actual ERCOT Dispatch Instruction with at least a 95% reduction in its Load within ten (10) minutes in the applicable calendar year, ERCOT will use that response in lieu of another actual interruption test.  QSEs may request to have individual LaaRs aggregated for the purposes of actual interruption tests.  All performance evaluations will apply on an individual Resource basis.

All Generation Resources and Loads acting as a Resource shall meet all requirements specified in the Operating Guides for proper response to system frequency.  ERCOT may reduce the amount a Resource may contribute toward Ancillary Services if it finds unsatisfactory performance of the Resource as defined in these Protocols and the Operating Guides.

Qualification of a Resource, including a Load acting as a Resource or an EILS Resource, shall remain valid for such Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.