ERCOT Operations Report

February 2008 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration |  |
| --- | --- | --- | --- |
| 2/1/08 6:59 | 60.142 | 11:53 | Out of DRS. Aggregate SCE +1371 MW. Wind SCE +550 MW. |
| 2/3/08 15:23 | 59.861 | 01:28 | Unit Trip with 770 MW online. |
| 2/3/08 21:20 | 59.896 | 00:04 | Steel Mill Load came up by 200 MW & System Load by 400 MW. |
| 2/7/08 4:53 | 60.101 | 00:08 | Out of DRS. Slower than expected system load pickup. |
| 2/8/08 5:03 | 59.816 | 00:44 | Unit Trip with 570 MW online. |
| 2/13/08 7:13 | 59.892 | 00:08 | Unit Trip with 700 MW online. |
| 2/15/08 5:48 | 60.105 | 00:18 | SCE + 400 MW caused by several QSEs |
| 2/15/08 6:16 | 59.899 | 00:06 | SCE drop of 400 MW. |
| 2/16/08 3:58 | 59.886 | 00:04 | SCE drop of 450 MW. |
| 2/16/08 13:29 | 59.895 | 01:08 | Unit Trip with 360 MW online |
| 2/19/08 3:05 | 59.844 | 01:18 | Wind unit trips with 250 MW online. |
| 2/20/08 22:59 | 59.839 | 00:08 | Unit Trip with 385 MW online |
| 2/22/08 4:39 | 59.893 | 00:02 | Unit Trip with 150 MW. |
| 2/24/08 18:16 | 60.108 | 00:40 | SCE +300 MW. Steel Mill drops 200 MW. |
| 2/25/08 0:40 | 60.144 | 02:15 | Wind SCE + 290 MW in a span of 2 seconds. |
| 2/26/08 18:40 | 59.897 | 02:44 | Out of URS and UBES and wind SCE was negative. EECP Step 2 event. |
| 2/26/08 18:52 | 60.105 | 02:52 | LAAR response. |
| 2/28/08 7:14 | 59.896 | 00:04 | Units with 250 MW online instructed to drop to 0 MW due to a forced transmission outage. |
| 2/28/08 10:54 | 60.113 | 00:08 | SCE +400 MW. Steel Mill drop 150 MW |
| 2/28/08 13:12 | 59.898 | 00:04 | SCE -600 MW. |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 2/1 14:38:44 | 2/1 14:49:38 | 0:10:54 | 328.10 | Out of URS. WIND SCE |
| 2/3 15:23:50 | 2/3 15:41:35 | 0:17:45 | 927.03 |  |
| 2/3 21:20:11 | 2/3 21:43:07 | 0:22:56 | 385.4 |  |
| 2/5 13:03:37 | 2/5 13:15:43 | 0:12:06 | 343.74 | SCE |
| 2/5 22:33:04 | 2/5 22:37:39 | 0:04:35 | 328.10 | SCE |
| 2/6 0:13:30 | 2/6 0:19:00 | 0:05:30 | 322.90 | SCE |
| 2/6 0:34:56 | 2/6 0:39:50 | 0:04:54 | 338.53 | Steel Mill Pickup |
| 2/6 23:32:34 | 2/6 23:51:24 | 0:18:50 | 317.69 | SCE and slow system load drop |
| 2/8 5:03:00 | 2/8 5:17:06 | 0:14:06 | 802.03 |  |
| 2/12 4:10:13 | 2/12 4:17:17 | 0:07:04 | 343.74 | Unit Trip |
| 2/12 15:02:46 | 2/12 15:11:48 | 0:09:02 | 343.74 | Unit Trip & SCE |
| 2/12 22:00:20 | 2/12 22:09:52 | 0:09:32 | 348.94 | SCE & Schedule Change |
| 2/13 7:12:52 | 2/13 7:18:58 | 0:06:06 | 406.24 |  |
| 2/13 23:10:07 | 2/13 23:19:27 | 0:09:20 | 348.94 | SCE |
| 2/14 6:07:35 | 2/14 6:15:23 | 0:07:48 | 322.9 | SCE & System Load Pickup |
| 2/14 22:06:45 | 2/14 22:11:51 | 0:05:06 | 322.9 | SCE & Schedule Change |
| 2/15 6:03:19 | 2/15 6:32:51 | 0:29:32 | 369.78 |  |
| 2/16 0:35:55 | 2/16 0:49:43 | 0:13:48 | 333.33 | Unit Trips |
| 2/16 3:58:59 | 2/16 4:05:38 | 0:06:39 | 437.47 |  |
| 2/16 10:00:45 | 2/16 10:24:31 | 0:23:46 | 348.94 | SCE |
| 2/16 13:29:13 | 2/16 13:43:51 | 0:14:38 | 390.6 |  |
| 2/17 0:42:59 | 2/17 0:54:45 | 0:11:46 | 333.33 | SCE |
| 2/18 4:10:02 | 2/18 4:16:22 | 0:06:20 | 343.74 | Out of URS due to a bad offset. |
| 2/19 3:06:01 | 2/19 3:17:33 | 0:11:32 | 656.21 |  |
| 2/20 22:59:19 | 2/20 23:13:26 | 0:14:07 | 682.25 |  |
| 2/22 4:39:44 | 2/22 4:46:12 | 0:06:28 | 401.01 |  |
| 2/23 18:40:50 | 2/23 18:50:34 | 0:09:44 | 343.74 | Out of URS & SCE |
| 2/24 21:58:46 | 2/24 22:05:00 | 0:06:14 | 343.74 | SCE & Schedule Change |
| 2/26 14:33:56 | 2/26 14:47:54 | 0:13:58 | 338.53 | Out of URS & Steel Mill Load Pickup |
| 2/26 18:33:05 | 2/26 18:56:06 | 0:23:01 | 642.97 |  |
| 2/27 7:10:29 | 2/27 7:14:00 | 0:03:31 | 333.33 | Unit Trips |
| 2/27 8:02:14 | 2/27 8:07:12 | 0:04:58 | 338.53 | SCE |
| 2/27 23:05:49 | 2/27 23:13:41 | 0:07:52 | 317.69 | Out of URS & Slow system load drop |
| 2/28 3:10:09 | 2/28 3:16:43 | 0:06:34 | 333.33 | Unit Trips |
| 2/28 7:14:50 | 2/28 7:17:32 | 0:02:42 | 385.4 |  |
| 2/28 12:39:45 | 2/28 12:46:33 | 0:06:48 | 317.69 | Unit Trips |
| 2/28 13:12:15 | 2/28 13:19:10 | 0:06:55 | 374.99 |  |
| 2/28 20:21:43 | 2/28 20:25:13 | 0:03:30 | 322.9 | SCE |
| 2/28 21:15:13 | 2/28 21:22:13 | 0:07:00 | 348.94 | Unit Trips |
| 2/29 8:23:06 | 2/29 8:29:49 | 0:06:43 | 322.9 | Unit Trips |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 0 | 5 | 6 | 11 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 |
| DFW | 0 | 1 | 0 | 7 | 8 |
| E RIO | 0 | 0 | 1 | 0 | 1 |
| Houston | 0 | 0 | 0 | 5 | 5 |
| Laredo | 38 | 0 | 0 | 0 | 38 |
| North | 0 | 2 | 4 | 2 | 8 |
| Northeast | 0 | 0 | 0 | 2 | 2 |
| San Antonio | 0 | 0 | 0 | 4 | 4 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 |
| Western | 0 | 0 | 8 | 8 | 16 |
|  | 38 | 3 | 18 | 34 | 93 |

| Historical Totals | Feb-07 | Jan-08 | Feb-08 |
| --- | --- | --- | --- |
| Austin | 4 | 3 | 11 |
| Bryan Area | 0 | 7 | 0 |
| Corpus | 1 | 0 | 0 |
| DFW | 16 | 4 | 8 |
| E RIO | 3 | 0 | 1 |
| Houston | 2 | 1 | 5 |
| Laredo | 48 | 51 | 38 |
| North | 3 | 5 | 8 |
| Northeast | 0 | 9 | 2 |
| San Antonio | 1 | 2 | 4 |
| South | 0 | 0 | 0 |
| W RIO | 58 | 0 | 0 |
| Western | 0 | 16 | 16 |
| Total | 136 | 98 | 93 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Matador - Paducah Clare Street/ SPUR 69kV | Matador - Paducah REA Tap 69kV | 6 |
| Mount Enterprise - Trinidad & Stryker Creek - Martin Lake 345kV | Nacogdoches 345/138kV Auto | 4 |
| Fisher Road - Oklaunion & Bowman 345kV | Abilene South - Putnam 138kV | 3 |
| Tricorner - Martin Lake & Forney Switch - Elkton 345kV | Elkton 345/138kV Auto #3 | 3 |
| Abilene South - Eskota 138kV | Trent - Scott REA Tap 69kV | 2 |
| Calaveras - Skyline & Walzem Road 138kV | Ballpark - Calaveras 138kV | 2 |
| Calaveras - Skyline & Walzem Road 138kV | Westside CPS - Five Points 138kV | 2 |
| Ingleside DuPont - Whitepoint 138kV | Whitepoint - Rincon 138kV | 2 |
| Snyder - China Grove Switch 138kV | Snyder - Scurry Santa Fe 69kV | 2 |
| Abilene East - Fort Phantom 138kV | Abilene South 138/69kV Auto #1 | 1 |
| Abilene Mulberry Creek - Bluff Creek 345kV | San Angelo Red Creek Auto #1 | 1 |
| Abilene Mulberry Creek - Oklaunion 345kV | Abilene South - Putnam 138kV | 1 |
| Comanche Switch - Comanche 345kV | Hood 138/69kV Auto #1 | 1 |
| Duke - Pharr Magic Valley 138kV | North Edinburg - Palm Hurst 138kV | 1 |
| Enterprise - Trinidad & Martin Lake - Stryker Creek 345kV | Elkton Auto | 1 |
| Garfield - Onion Creek & Hicross 138kV | Austrop - Daffin Gin 138kV | 1 |
| Garfield - Onion Creek & Hicross 138kV | Rohr - Canyon 138kV | 1 |
| Leon Switch - Putnam 138kV | Leon Switch 138/69kV Auto #5 | 1 |
| McDonald - Morgan Creek 138kV | McDonald - Forsan Tap 138kV | 1 |
| Menard - Gillespie 138kV | Castel - Fredonia 69kV | 1 |
| Morgan Creek SES - Tonkawa Switch 345kV | Abilene South - Pecan Bayou 138kV | 1 |
| Morgan Creek SES - Tonkawa Switch 345kV | China Grove Switch - Radium 138kV | 1 |
| North Edinburg - Lon Hill 345kV | Lon Hill - Nelson Sharp 345kV | 1 |
| San Angelo Red Creek - Bluff Creek 345kV | Abilene Mulberry Creek East Reactor Series 138kV | 1 |
| San Angelo Red Creek 345/138kV Auto #1 | San Angelo Red Creek 345/138kV Auto #2 | 1 |
| South Abilene - Eskota Switch 138kV | Trent - Merkel 69kV | 1 |
| Spur-Aspermont 138kV | Paducah - Matador 69kV | 1 |
| Trinidad SES Stryker Creek SES & Mount Enterprise 345kV | Athens Tap - Athens North Tap 138kV | 1 |
| Trinidad SES - Mount Enterprise 345kV | Athens tap - Athens North Switch 138kV | 1 |
| Twinbutte 345/138kV Auto | San Angelo Red Creek Auto #1 | 1 |
| West Levee 345/138kV Auto #1 | West Levee 345/138kV Auto #2 | 1 |
| Weatherford West - Miller 138kV | Hill Top 138/69kV Auto | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 24 |
| North-West | 15 |
| North-South | 4 |
| South-North | 2 |

New RAP

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 02/29/2008 | Shift Supervisor Desk, V3R45 | 365 |
| 02/23/2008 | Transmission and Security Desk V3 Rev89 | 362 |
| 02/23/2008 | Frequency Control Desk V3 Rev63 | 361 |
| 02/15/2008 | Shift Supervisor Desk V3 Rev44 | 364 |
| 02/15/2008 | Operating Period Desk V2 Rev23 | 363 |
| 02/09/2008 | Frequency Control Desk V3 Rev62 | 360 |
| 02/09/2008 | Shift Supervisor Desk V3 Rev43 | 359 |
| 02/09/2008 | Transmission and Security Desk V3 Rev88 | 358 |

## Blackout/Load Shed Incidences

None

EECP

02/26 18:41	EECP Step 2 initiated.

Major System Voltage Problems

2/08	09:36	Voltage deviation greater than 5% at Long Creek 345kV bus.

2/18	02:19	Voltage deviation greater than 5% at Long Creek 345kV bus.

2/22     14:06   Voltage deviation greater than 5% at Long Creek 345kV bus.

Major Computer Problems, Enhancements & Fixes

2/5 	Held the 10:00 interval, resumed with the 10:30 interval due to database maintenance issues.

2/23 	Held interval 17:15 deployments, resumed with 17:45 interval due to Real Time Balancing Market failed to approve.

2/25  	Held interval 19:00 deployments, resumed with 19:30 interval due to Real Time Balancing Market failed.

Communication

None

## ERCOT peak (Unofficial)

02/01 	   07:00  45,274 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | 3.59 |
| March | 3.41 | 4.95 | 2.70 | NA |
| April | 3.37 | 5.59 | 3.00 | NA |
| May | 4.21 | 3.59 | 3.22 | NA |
| June | 3.91 | 2.65 | 4.46 | NA |
| July | 5.22 | 2.62 | 4.29 | NA |
| August | 4.86 | 2.09 | 3.11 | NA |
| September | 6.24 | 4.03 | 3.78 | NA |
| October | 4.51 | 3.63 | 3.08 | NA |
| November | 4.53 | 3.28 | 2.95 | NA |
| December | 5.95 | 3.44 | 3.74 | NA |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.44 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Subject | Event |
| --- | --- | --- | --- | --- |
| 2/1/08 | 0:15 | 7:39 | Advisory | Advisory ARR below 3000 MW. |
| 2/2/08 | 3:40 | 13:08 | Advisory | Advisory ARR below 3000 MW. |
| 2/4/08 | 18:20 | 20:47 | Advisory | Advisory ARR below 3000 MW. |
| 2/5/08 | 11:09 | 20:52 | Advisory | Advisory ARR below 3000 MW. |
| 2/6/08 | 6:50 | 9:48 | Advisory | Advisory ARR below 3000 MW. |
| 2/8/08 | 7:00 | 7:53 | Advisory | Advisory ARR below 3000 MW. |
| 2/9/08 | 18:55 | 19:50 | Advisory | Advisory ARR below 3000 MW. |
| 2/10/08 | 18:15 | 20:30 | Advisory | Advisory ARR below 3000 MW. |
| 2/14/08 | 18:50 | 21:00 | Advisory | Advisory ARR below 3000 MW. |
| 2/21/08 | 9:35 | 20:00 | Advisory | Advisory ARR below 3000 MW. |
| 2/23/08 | 2:08 | 11:10 | Advisory | Advisory ARR below 3000 MW. |
| 2/24/08 | 18:45 | 23:00 | Advisory | Advisory ARR below 3000 MW. |
| 2/25/08 | 18:45 | 22:30 | Advisory | Advisory ARR below 3000 MW. |
| 2/26/08 | 18:24 | 22:44 | Advisory | Advisory ARR below 3000 MW. |
| 2/26/08 | 18:41 | 21:40 | Emergency | EECP Step 2 Initiated. |
| 2/27/08 | 7:03 | 8:00 | Advisory | Advisory ARR below 3000 MW. |

Other

1/04     13:36	Matador SPS armed and actuated at Whirlwind Energy Center.

1/09	15:45	Monticello Mining SPS armed and actuated

1/15	17:04	McDonald Road SPS armed and actuated.

1/21	07:14	McDonald Road SPS armed and actuated

1/21	10:04	Matador SPS armed and actuated at Whirlwind Energy Center

1/23 	19:45	Matador SPS armed and actuated at Whirlwind Energy Center.

1/26	04:57	Matador SPS armed and actuated at Whirlwind Energy Center.

2/19     03:06 Transformer Differential relay on Abilene Mulberry Creek Auto WH,       causing loss of 650 MW of generation and the Oklaunion – Abilene Mulberry Creek 345 kV line, Abilene Mulberry Creek – Long Creek 345 kV line and Abilene Mulberry Creek – Bluff Creek 345 kV line.

2/24    19:53     SPS activation at Golden Switch.

2/28    07:09	Tripped Abilene Mulberry Creek 345 kV bus & Auto along with 345kV lines to Bitter Creek, Long Creek and Bluff Creek.

2/28     07:12    Matador SPS Activation at Whirlwind Energy Center.