## 3-16-08
Time | Possible Explanations for Poor Correlations
11:37 | At 11:37:56, there was a unit trip and the frequency dropped in the Nodal system to 59.72. The frequency drop was not caught in the Zonal system until a 4 second scan later. The values between Nodal and Zonal varied so greatly for during this single scan that the correlation was significantly lowered for the entire 10 minute period.

## 3-17-08
Time | Possible Explanations for Poor Correlations
12:10 | Nodal frequency was frozen at 60.053001 for 12:10:16 until 12:17:56
18:00 | Nodal frequency was frozen at 60.001999 for 18:01:32 until 18:06:12
18:20 | Nodal frequency was frozen at 60.26001 for 18:18:04 until 18:19:48. The frequency was then set at 60.035 and stayed there fom 18:19:52 until 18:22:48. Later then frequency was set at 59.978001 from 18:24:04 until 18:26:04.

## 3-18-08
Time | Possible Explanations for Poor Correlations
8:30 - 12:00 | From 8:30 until 12:00, ERCOT was performing time error correction and were controlling to 59.98 Hz.
10:00 | The Nodal frequency was frozen at 59.947 from 10:03:24 until 10:08:08.
16:50 | The Nodal frequency was frozen at 59.95 from 16:50:36 until 16:59:56.

## 3-19-08
Time | Possible Explanations for Poor Correlations
9:30 - 10:50 | The Nodal frequency was frozen at 60.022 from 09:33:32 until 10:50:40.
10:50 - 11:15 | The Nodal frequency was frozen at 60.041 from 10:50:44 until 11:16:56.
13:10 | The Nodal frequency was frozen at 59.995 from 13:10:00 until 13:22:44 and then at 60.037 from 13:22:48 until 13:24:16.
15:00 - 15:20 | The Nodal frequency was frozen at 60.036 from 15:04:04 until 15:21:12.
16:10 | The Nodal frequency was frozen at 60.03 from 16:13:36 until 16:21:56.

## 3-20-08
Time | Possible Explanations for Poor Correlations
No issues

## 3-21-08
Time | Possible Explanations for Poor Correlations
13:40 | The Nodal frequency was frozen at 60.011 from 13:46:32 until 13:55:08.
14:30 -16:20 | The Nodal frequency was frozen at 60.038 from 14:35:40 until 16:19:16 and then on 59.992 from 16:19:20 until 16:20:52.

## 3-22-08
Time | Possible Explanations for Poor Correlations
No issues