| OGRR Number | 205 | OGRR Title | Modify Responsive Reserve Service Obligation |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | April 4, 2008 |  |  |
| Operating Guide Sections Requiring Revision |  | 1.5, Conformance to NERC Policies, Procedures, and Reliability Standards 2.5.2.1, Obligation |  |  |
| Effective Date |  | ## May 1, 2008 |  |  |
| Priority & Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) clarifies that the minimum ERCOT Responsive Reserve Obligation is 2300 MW. |  |  |
| ###### Overall Market Benefit |  | Clarification. |  |  |
| ###### Overall Market Impact |  | Unknown. |  |  |
| ###### Consumer Impact |  | Unknown. |  |  |
| ###### Procedural History |  | - On 10/03/07, OGRR205 was posted. - On 12/05/07, Impact Analysis (IA) was posted. - On 01/15/08, Operating Guides Revision Task Force (OGRTF) comments were posted. - On 01/16/08, Operations Working Group (OWG) considered OGRR205. - On 02/20/08, OWG considered the Recommendation Report and the IA. - On 3/13/08, ROS considered OGRR205. - On 4/4/08, TAC considered OGRR205. |  |  |
| ###### OWG Decision |  | On 01/16/08, the OWG was in consensus to recommend approval of OGRR205 as revised by the OGRTF comments. On 02/20/08, the OWG was in consensus to forward the Recommendation Report and the IA to ROS for approval. |  |  |
| ###### Summary of OWG Discussion |  | On 01/16/08, there was no discussion. On 02/20/08, there was no discussion. |  |  |
| ###### ROS Decision |  | On 3/13/08, ROS unanimously voted to recommend approval of OGRR205 as recommended by OWG. All Market Segments were present for the vote. |  |  |
| ###### Summary of ROS Discussion |  | On 3/13/08, OWG presented its Recommendation Report for OGRR205. |  |  |
| TAC Decision |  | On 4/4/08, TAC unanimously voted to approve OGRR205 as recommended by ROS. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 4/4/08, there was no discussion. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Assume 2800 MW of RRS for every hour of every day. An option may be to only increase to 2800 MW for certain hours (ex. 0600 – 2200). |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | Not known. | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Allow for better market price resolution before command and control action. | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |
|  | 3 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | Gary D. Miller (on behalf of Qualified Scheduling Entities (QSE) Managers Working Group) |
| E-mail Address | gmiller@btutilities.com |
| Company | Bryan Texas Utilities (BTU) |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 011508 | Clarified that the ERCOT Responsive Reserve Obligation is a minimum of 2300 MW. |

Proposed Operating Guide Language Revision

## 1.5	Conformance to NERC Policies, Procedures, and Reliability Standards

The Electric Reliability Council of Texas (ERCOT) Operating Guides are for the purpose of outlining specific practices for the ERCOT System.  These practices are consistent with the North American Electric Reliability Corporation (NERC) Operating Policies and standards.  For application in ERCOT, some NERC Policies must be adapted to fit the unique characteristics of the ERCOT System.  Specific necessary adaptations are listed below:

| NERC Policy | ERCOT Adaptation |
| --- | --- |
| Time and Frequency Control | Sustained frequency deviations from 60 Hz result in time error. |
| - Time Error Monitoring | ERCOT will monitor accumulated time error and initiate time corrections. The instantaneous time error is available to all ERCOT QSEs in the ERCOT website. When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction; however, at no time should the accumulated time error be allowed to exceed five (5) seconds. |
| - Time Error Correction | When a time correction is necessary, ERCOT will adjust scheduled frequency in the following manner. ERCOT will arrange for more or less resources. Information to be passed along will include the correction frequency (59.98 Hz for fast and 60.02 Hz for slow) and the start time. A time correction may be terminated after five (5) hours, after any hour without a one-half (0.5) second error reduction. The Control Area Authority will provide adequate notice of ending the time correction. |
| Inadvertent Interchange Management | The only Inadvertent Energy will be between ERCOT and SPP and/or CFE. Accounting / payback will be handled according to NERC policy. The hourly difference between a Control Area’s actual net interchange and a Control Area’s scheduled net interchange is classified as inadvertent energy. All inadvertent energy is placed in an Inadvertent Payback Account to be paid back in kind. |
| Control Surveys | Not all of the surveys defined by NERC apply to a system the size of ERCOT and /or a single Control Area interconnection such as ERCOT. |
| Load Shedding and System Restoration | Automatic firm Load shedding will be initiated as follows: Frequency % Load Relief 59.3 Hz 5% 58.9 Hz 10% 58.5 Hz 10% Load shedding will be widely dispersed in each TDSP, with no preference to LSEs, and will be accomplished by using high-speed under-frequency relays. The frequency measuring relays shall have a time delay of no more than 30 cycles (or 0.5 seconds for relays that do not count cycles). If the frequency and time values are reached, an irretrievable trip is initiated. Total time from the time when frequency first reaches one of the values specified above to the timeLoad is interrupted should be no more than 40 cycles, including all relay and breaker operating times. Under-frequency relays may be installed on Transmission Facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. Load restoration will be under the direction of the ERCOT Control Area Authority. A TDSP may by mutual agreement, with the approval of the TAC, arrange to have all or part of its automatic Load shedding obligation carried by another TDSP. ERCOT will be notified and provided with the details of any such arrangement prior to implementation. |
| Information Exchange – Disturbance Reporting | ERCOT will record the following data from the ERCOT System for frequency deviations of .175 Hz or greater and will use this information to generate the ERCOT initial Disturbance Report: - ERCOT and individual QSE control biases. - Net MW Capability (including any capability lost) at the time of the disturbance. - Net System Load (MW) for the hour ending closest to the time of the disturbance. - Scheduled Net Interchange (MW) at the time of the disturbance. - Amount of interruptible load (MW) tripped. Reference: Protocol Section 6.10.5.4, Responsive Reserve Services Deployment Performance Monitoring Criteria (In Part) …For all frequency deviations exceeding 0.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve Service. ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event or Manual / Dispatch Instruction until ten (10) minutes after the start of the frequency excursion event or Manual / Dispatch Instruction… |
| Reliability Criteria | ERCOT operating reserve requirements are more restrictive than the concepts in the NERC Operating Manual. The ERCOT Responsive Reserve Obligation is a minimum of 2300 MW. |

#### 2.5.2.1	    Obligation

The ERCOT Responsive Reserve Obligation is a minimum of 2300 MW.