## Slide 1: ERCOT SCR745 Update ERCOT Outage Evaluation Phase 1 and Phase 2
RMS
April 9, 2008

## Slide 2: PR60006_01 ERCOT Update
Background:
SCR 745: To achieve improved Market performance and reliability through a reduction of ERCOT Retail Systems unplanned outages. Achieve 99.99% Availability within Paperfree Application
  This effort was planned to be implemented in two subprojects;
    PR60006_01: ERCOT Outage Evaluation Phase I and Phase II
    Phase I, NAESB and Proxy Clustered (Delivered 02/2007)
    Phase II, Paperfree Clustered environment with File Server Redundancy
    PR60006_02: Phase III, Database Clustered environment (below PPL cut line for 2008)
Phase II Current Status:
02/27/2008 – Integration, Performance/Volume and Failover Testing
03/08/2009 – Production Implementation
03/22/2008 – Rollback to previous Paperfree Infrastructure due to Performance Issues

## Slide 3: PR60006_01 ERCOT Update - Continued
Testing Results:
11 High Availability / Fault tolerance tests - complete.
  1 related open defect; to be addressed in future release(s).
    Description: Node Fencing on shutdown from RSA results in application failure.
Steady transaction flow volume test – completed.
Despite open defect with PolyServe software, the advantages provided would include:
  File Server Redundancy
    Addresses the identified single point of failure for loss of Mapping for users and application processes.
    Allows for maintenance capabilities without affecting all nodes in cluster
  High Availability / Fault Tolerance
  Clustered Load Balancing

## Slide 4: PR60006_01 ERCOT Update - Continued
Date | Description | Resolution | Root Cause
03/12/2008 | Retail Application Outage | Restart processes in order | Human Error (See SLA Update)
03/12/2008 | 867 files not loading into L* | Permissions were granted | Permissions issue (See SLA Update)
03/19/2008 | Hard Crash of Polyserve Cluster due to SAN Switch Failure | Moved Polyserve cluster to different switch | SAN Switch Failure caused Node Fencing: If polyserve loses connectivity to SAN, the cluster will lock. HP Ticket logged 12/11/2007 (see slide 3).
03/12/2008 – 03/22/2008 | Paperfree Performance degradation | 03/19/2008 Implemented SIR 11823 to add additional transaction processing enhancements. 03/22/20008 Rollback to old infrastructure until performance tuning recommendations from HP can be implemented / tested | Unknown

## Slide 5: PR60006_01 ERCOT Update - Next Steps
Roll iTEST back to old infrastructure of Paperfree Fan Out (Blades). Required to mitigate impact to PR60008: Ts&Cs and PUCT 33049 Performance Measures – Complete
TDTWG Meeting to discuss issues – Complete.
Analyze performance tuning options provided by HP for feasibility.
Discuss Plans to move forward with effort on SCR745 and re-implementation of Polyserve at ERCOT with TDTWG May, 2008
Things to take consider for future discussion:
PaperFree Availability Metrics (Prior to March 2008 Incidents)
Previous Logged incident for PaperFree file server – 02/2007.
02/2008 – 100% availability (meeting SCR Goal).
2007 Intermediate Resolutions
Code Changes
  File Management (Copy / Move / Delete) Retry
  Re-Map drives before processing vs. application startup
Hardware Replacement
  Implementation of 3950 (4-Way) server for file server
Increased Training
Increased Monitoring
Future discussion at TDTWG - Does the 2007 Intermediate Resolutions meet the objective of the SCR745 Phase II Goals?

## Slide 6: PR60006_02 ERCOT Update
PR60006_02: Phase III, Database Clustered environment
Recommendation from ERCOT to TDTWG to Cancel this project – Resolved with AIX deployment
Last Incident logged – 01/05/2008
02/2008 – 100% Availability