## Slide 1: Collected Comments For Possible Further Action EECP Step#2 Event/2-26-2008
4/10/08
EECP Event 2/26/2008

## Slide 2: Request to ROS
EECP Event 2/26/2008
4/10/08
At the March ROS meeting, Texas RE requested that ROS develop recommendations for further action, study or follow-up related to this event.
Texas RE collected comments for ROS to discuss at their April meeting
ROS is asked to review items on the list, modify as necessary, and vote approval for those items meriting additional follow-up by working groups, ERCOT staff or other entities

## Slide 3: Possible Recommendation 1
Determine how the wind generation forecast that will be a part of Nodal can be integrated into current Zonal operations planning.
EECP Event 2/26/2008
4/10/08

## Slide 4: Possible Recommendation 2
EECP Event 2/26/2008
4/10/08
Begin modifying the handling of the day-ahead and the short-term load forecasting process by building an hourly load and weather database and using days other than yesterday to forecast tomorrow.

## Slide 5: Possible Recommendation 3
EECP Event 2/26/2008
4/10/08
Hire an experienced energy market meteorologist to work with ERCOT ISO on daily wind and load forecasting and to be on call for weekend weather events.

## Slide 6: Possible Recommendation 4
EECP Event 2/26/2008
4/10/08
Procure blocks of NSRS on a day-ahead basis to cover only certain hours of forecasted major weather frontal passage

## Slide 7: Possible Recommendation 5
Review the expectations on Resource Plan updates for uncontrollable renewable resources and provide additional guidance. All QSEs, including wind QSEs, MUST be vigilant in updating their Resource Plan and keeping it accurate.
EECP Event 2/26/2008
4/10/08

## Slide 8: Possible Recommendation 6
Establish a prescribed ramp rate for wind farms’ ramping up production after completion of an OOM-E Down instruction in order to apply controls to the near term frequency oscillations seen in the system.
EECP Event 2/26/2008
4/10/08

## Slide 9: Possible Recommendation 7
EECP Event 2/26/2008
4/10/08
Re-examine the exclusion from SCE performance metrics granted to wind farms and determine an alternative to these metrics and penalties. Possibilities to consider include:
  Set a realistic 10-minute performance metric for Wind-Only QSEs in the range of 50-60 percent
  Eliminate the Wind-Only QSE Category
  Establish a methodology for purchase of supplemental regulation service from another QSE through the existing Responsibility Transfer provision already in the Protocols.

## Slide 10: Possible Recommendation 8
EECP Event 2/26/2008
4/10/08
Study the amount of machine inertia or substitutable response needed for the various amounts of wind penetration and begin a discussion of how to manage unit commitment in zonal and nodal to achieve the minimum.

## Slide 11: Possible Recommendation 9
EECP Event 2/26/2008
4/10/08
Explore the concept of requiring storage companion capabilities (i.e., similar to pumped hydro) for any new wind beyond the legislative RPS level.

## Slide 12
4/10/08
EECP Event 2/26/2008