ERCOT Operations Report

March 2008 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 3/1/2008 5:50 | 60.104 | 34 | Out of DRS & slow load growth |
| 3/1/2008 10:13 | 59.89 | 8 | Unit trip with 317 MW online |
| 3/1/2008 10:58 | 60.116 | 80 | SCE change +650 MW |
| 3/1/2008 11:10 | 60.107 | 28 | Out of DRS, SCE change +200 MW & Steel Mill load drop 250 MW |
| 3/2/2008 0:03 | 60.107 | 404 | Out of DRS & SCE change 350 MW |
| 3/2/2008 2:27 | 60.118 | 32 | SCE change +400 MW & Steel Mill load drop 100 MW |
| 3/3/2008 1:16 | 60.109 | 26 | SCE change +350 MW & Steel Mill load drop 150 MW |
| 3/3/2008 10:08 | 59.875 | 14 | Multiple Unit trips with 495 MW online |
| 3/3/2008 10:31 | 60.107 | 417 | Frequency at 60.13 due to large balancing ramp to offset unit loss |
| 3/4/2008 4:14 | 59.881 | 2 | Multiple Unit trips with 550 MW online |
| 3/4/2008 23:16 | 59.888 | 18 | Multiple Unit trips with 410 MW online |
| 3/9/2008 20:30 | 59.832 | 40 | Unit trip with 550 MW online |
| 3/12/2008 0:05 | 60.101 | 4 | SCE change +350 MW & Steel Mill load drop 100 MW |
| 3/12/2008 6:12 | 59.898 | 4 | SCE change -700 MW |
| 3/12/2008 22:05 | 59.895 | 2 | SCE change -600 MW |
| 3/13/2008 0:35 | 60.117 | 218 | Out of DRS & no offset was entered due to held interval. |
| 3/13/2008 4:58 | 60.107 | 8 | SCE change +400 MW & Steel Mill drop 100 MW |
| 3/13/2008 6:48 | 60.118 | 94 | QSEs recovering SCE while up-balancing |
| 3/13/2008 9:16 | 59.873 | 64 | Unit trip with 640 MW online |
| 3/13/2008 9:28 | 59.89 | 134 | Out of URS due to response of Unit trip, SCE change -400 MW |
| 3/14/2008 3:57 | 59.899 | 2 | Out of URS, SCE change -350 MW & Steel Mill load pickup 200 MW |
| 3/14/2008 4:34 | 60.113 | 274 | SCE change +600 MW |
| 3/14/2008 4:46 | 60.104 | 80 | SCE change +400 MW & Steel Mill load drop 100 MW |
| 3/16/2008 11:37 | 59.806 | 58 | Unit trip with 1170 MW online |
| 3/17/2008 19:04 | 60.106 | 60 | SCE +450 MW at the time frequency spike and kept on increasing |
| 3/21/2008 10:37 | 60.101 | 24 | SCE change +500 MW |
| 3/22/2008 17:38 | 59.891 | 4 | Out of URS & SCE change -300 MW |
| 3/24/2008 21:17 | 60.104 | 338 | Input error in offset calculation |
| 3/28/2008 14:55 | 59.894 | 2 | Unit trip with 395 MW online |
| 3/29/2008 5:58 | 60.102 | 132 | MOI froze & no offset was entered |
| 3/30/2008 1:17 | 60.102 | 708 | Out of DRS & SCE Change +400 MW |
| 3/30/2008 8:33 | 59.822 | 52 | Unit trip with 770 MW online |
| 3/1/2008 5:50 | 60.104 | 34 | Out of DRS and slow growth in load |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 3/1 6:03:06 | 3/1 6:23:03 | 0:19:57 | 333.33 | SCE |
| 3/1 10:10:11 | 3/1 10:24:33 | 0:14:22 | 416.65 |  |
| 3/1 21:03:01 | 3/1 21:07:45 | 0:04:44 | 322.9 | Units following OOME instruction down immediately |
| 3/1 22:15:31 | 3/1 22:24:25 | 0:08:54 | 317.69 | Units trip |
| 3/2 2:15:35 | 3/2 2:29:08 | 0:13:33 | 343.74 | Unit trip |
| 3/2 16:19:53 | 3/2 16:25:49 | 0:05:56 | 317.69 | SCE & Steel Mill Pickup |
| 3/3 8:15:17 | 3/3 8:29:55 | 0:14:38 | 322.9 | SCE |
| 3/3 10:08:46 | 3/3 10:23:37 | 0:14:51 | 494.77 |  |
| 3/4 4:14:28 | 3/4 4:33:09 | 0:18:41 | 463.52 |  |
| 3/4 23:16:46 | 3/4 23:23:47 | 0:07:01 | 427.06 |  |
| 3/7 18:39:38 | 3/7 19:00:02 | 0:20:24 | 317.69 | SCE & Steel Mill Pickup |
| 3/9 20:30:56 | 3/9 20:43:04 | 0:12:08 | 718.71 |  |
| 3/10 10:16:14 | 3/10 10:23:58 | 0:07:44 | 322.9 | SCE |
| 3/11 5:03:48 | 3/11 5:08:32 | 0:04:44 | 338.53 | SCE & Steel Mill Pickup |
| 3/11 5:10:36 | 3/11 5:15:40 | 0:05:04 | 328.1 | SCE |
| 3/11 6:09:14 | 3/11 6:19:36 | 0:10:22 | 322.9 | Out of URS & SCE |
| 3/11 19:54:30 | 3/11 20:14:14 | 0:19:44 | 348.94 | Out of URS & SCE |
| 3/12 6:06:36 | 3/12 6:29:18 | 0:22:42 | 374.99 |  |
| 3/12 22:06:00 | 3/12 22:18:22 | 0:12:22 | 390.6 |  |
| 3/13 9:16:14 | 3/13 9:46:24 | 0:30:10 | 739.55 |  |
| 3/13 9:49:50 | 3/13 9:58:30 | 0:08:40 | 333.33 | Out of URS due to response of Unit trip 34 min earlier. |
| 3/13 15:12:46 | 3/13 15:27:06 | 0:14:20 | 328.1 | Steel Mill Pickup & SCE |
| 3/13 19:25:01 | 3/13 20:00:58 | 0:35:57 | 322.9 | Out of URS & SCE |
| 3/13 21:59:46 | 3/13 22:15:48 | 0:16:02 | 333.33 | Steel Mill Pickup & SCE |
| 3/14 3:57:48 | 3/14 4:07:24 | 0:09:36 | 369.78 |  |
| 3/16 11:37:58 | 3/16 12:01:02 | 0:23:04 | 864.53 |  |
| 3/17 8:55:04 | 3/17 9:03:58 | 0:08:54 | 328.1 | Unit trip |
| 3/18 0:44:10 | 3/18 0:53:38 | 0:09:28 | 317.69 | Out of URS & SCE |
| 3/19 6:08:10 | 3/19 6:13:58 | 0:05:48 | 338.53 | SCE |
| 3/19 9:05:26 | 3/19 9:21:46 | 0:16:20 | 364.56 | SCE |
| 3/21 9:52:20 | 3/21 10:23:06 | 0:30:46 | 359.35 | Out of URS & SCE |
| 3/21 22:47:10 | 3/21 23:02:02 | 0:14:52 | 354.15 | Unit trip |
| 3/22 16:07:10 | 3/22 16:27:50 | 0:20:40 | 317.69 | Out of URS & SCE |
| 3/22 17:38:14 | 3/22 17:49:04 | 0:10:50 | 411.44 |  |
| 3/22 19:54:44 | 3/22 20:08:16 | 0:13:32 | 348.94 | Out of URS & SCE |
| 3/26 20:18:36 | 3/26 20:25:50 | 0:07:14 | 401.01 | Unit trip |
| 3/27 22:05:16 | 3/27 22:24:38 | 0:19:22 | 322.9 | SCE |
| 3/27 23:05:30 | 3/27 23:14:58 | 0:09:28 | 359.35 | Steel Mill Pickup & SCE |
| 3/28 14:55:12 | 3/28 15:14:48 | 0:19:36 | 395.81 |  |
| 3/30 8:33:22 | 3/30 8:55:54 | 0:22:32 | 770.8 |  |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 3 | 5 | 2 | 10 |
| Bryan Area | 0 | 7 | 0 | 0 | 7 |
| Corpus | 0 | 1 | 0 | 1 | 2 |
| DFW | 0 | 5 | 0 | 1 | 6 |
| E RIO | 0 | 8 | 11 | 0 | 19 |
| Houston | 0 | 3 | 0 | 4 | 7 |
| Laredo | 59 | 0 | 0 | 0 | 59 |
| North | 0 | 1 | 1 | 2 | 4 |
| Northeast | 0 | 10 | 0 | 0 | 10 |
| San Antonio | 0 | 0 | 0 | 2 | 2 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 |
| Western | 0 | 44 | 16 | 0 | 60 |
|  | 59 | 82 | 33 | 12 | 186 |

| Historical Totals | Mar-07 | Feb-08 | Mar-08 |
| --- | --- | --- | --- |
| Austin | 11 | 11 | 10 |
| Bryan Area | 0 | 0 | 7 |
| Corpus | 0 | 0 | 2 |
| DFW | 6 | 8 | 6 |
| E RIO | 7 | 1 | 19 |
| Houston | 7 | 5 | 7 |
| Laredo | 56 | 38 | 59 |
| North | 4 | 8 | 4 |
| Northeast | 4 | 2 | 10 |
| San Antonio | 4 | 4 | 2 |
| South | 8 | 0 | 0 |
| W RIO | 66 | 0 | 0 |
| Western | 22 | 16 | 60 |
| Total | 195 | 93 | 186 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| North Edinburg - Rio Hondo 345kV | South McAllen - Las Milpas 138kV | 6 |
| Moss Switch - Holt Switch 138kV | Odessa North - North Cowden 69kV | 5 |
| Everman SW - Decordova SES - Rocky Creek 345kV | Benbrook SW 345/138kV Auto | 2 |
| Fisher Road Switch -Oklaunion & -Bowman 345kV | Bomarton - Seymour 69kV | 2 |
| Lytton Springs & Austrop - Zorn 345kV | Canyon - Rohr 138kV | 2 |
| Divide Switchyard - Gasconades Creek 345kV | Sterling City - Sterling County 69kV | 2 |
| Lon Hill - North Edinburg 345kV | Alazan - Nelson Sharp 138kV | 2 |
| Rio Hondo - LaPalma 138kV | South McAllen - Las Milpas 138kV | 2 |
| San Angelo Red Creek - Bluff Creek 345kV | Graham SW - Long Creek 345kV | 2 |
| Temple SW - Killeen SW & Sandow SW 345kV | Harker Heights South - Killeen SW 138kV | 2 |
| Temple SW - Tradinghouse SES - Lake Creek SES 345kV | Menard 138/69kV Auto | 2 |
| Hamilton Road - Sonora 138kV | Sonora - Friess Ranch 69kV | 1 |
| Hamilton Road - Sonora 138kV | Friess Ranch - Rocksprings 69kV | 1 |
| Hoffman - West Columbia 138kV | Sealy - Wallis 138kV | 1 |
| Jewett - TH Wharton & Tomball 345kV | Watson Chapel - Robertson 138kV | 1 |
| Lon Hill - Coleto Creek 345kV | Victoria - Warburton 138kV | 1 |
| Lon Hill - North Edinburg 345kV | Kingsville - Lon Hill 138kV | 1 |
| Martin Lake SES - Stryker Creek SES & Mt. Enterprise 345kV | Nacogdoches SE 345/138kV Auto | 1 |
| North Edinburg - Rio Hondo 345kV | South McAllen - Stewart Road 138kV | 1 |
| Rio Hondo - LaPalma 138kV | Raymondville 2 - Raymondville 1 69kV | 1 |
| Tonkawa Switch - Graham SES 345kV | Abilene South - Putnam 138kV | 1 |
| Tricorner - Martin Lake SES & Forney Switch - Elkton 345kV | Athens Tap - Athens North Switch 138kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 28 |
| North-South | 13 |
| South-North | 9 |
| North-Houston | 4 |
| North –West | 2 |

New RAP

None

New Procedures/Forms/Operations Bulletins

None

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

3/22     01:47	Voltage deviation greater than 5% at Sweetwater Generating Station 345 kV bus.

Major Computer Problems, Enhancements & Fixes

3/16 	RPRS Market for 03/17/08 failed to clear by the 1800 Timeline due to forced outage equipment shown online in the case.

Communication

None

## ERCOT peak (Unofficial)

03/13 	   08:00 42,313 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | 3.59 |
| March | 3.41 | 4.95 | 2.70 | 3.29 |
| April | 3.37 | 5.59 | 3.00 | NA |
| May | 4.21 | 3.59 | 3.22 | NA |
| June | 3.91 | 2.65 | 4.46 | NA |
| July | 5.22 | 2.62 | 4.29 | NA |
| August | 4.86 | 2.09 | 3.11 | NA |
| September | 6.24 | 4.03 | 3.78 | NA |
| October | 4.51 | 3.63 | 3.08 | NA |
| November | 4.53 | 3.28 | 2.95 | NA |
| December | 5.95 | 3.44 | 3.74 | NA |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.39 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 3/1/08 | 9:10 | 14:15 | Advisory ARR below 3000 MW. |
| 3/2/08 | 18:29 | 21:30 | Advisory ARR below 3000 MW. |
| 3/2/08 | 18:40 | 21:30 | Deployed NSRS in North, South and Houston zones due to declining Adjusted Responsive Reserve. AWS forecast showed wind dropping to 600 MW with current wind generation at 2500 MW. |
| 3/3/08 | 18:28 | 21:30 | Advisory for Adjusted Responsive Reserve less than 3000 MW. |
| 3/3/08 | 18:39 | 21:30 | Deployed NSRS in all zones due to depletion of up balancing bids. |
| 3/4/08 | 6:25 | 7:30 | Advisory ARR below 3000 MW. |
| 3/5/08 | 6:35 | 7:30 | Advisory ARR below 3000 MW. |
| 3/6/08 | 16:45 | 22:30 | Advisory ARR below 3000 MW. |
| 3/6/08 | 18:40 | 20:30 | Deployed NSRS in the North and West Zones due to projected depletion of up balancing. |
| 3/8/08 | 0:04 | 11:37 | Advisory ARR below 3000 MW. |
| 3/8/08 | 23:16 | 0:00 | Advisory ARR below 3000 MW. |
| 3/9/08 | 0:15 | 6:15 | Advisory ARR below 3000 MW. |
| 3/10/08 | 7:11 | 23:00 | Advisory ARR below 3000 MW. |
| 3/11/08 | 6:52 | 12:20 | Advisory ARR below 3000 MW. |
| 3/13/08 | 19:27 | 21:45 | Deployed NSRS due to projected depletion of balancing up bids. |
| 3/13/08 | 22:12 | 0:00 | Advisory ARR below 3000 MW. |
| 3/14/08 | 0:15 | 01:30 | Advisory ARR below 3000 MW. |
| 3/15/08 | 14:55 | 22:30 | Advisory ARR below 3000 MW. |
| 3/17/08 | 12:02 | 0:00 | Advisory ARR below 3000 MW. |
| 3/18/08 | 0:15 | 2:10 | Advisory ARR below 3000 MW. |
| 3/31/08 | 7:30 | 9:30 | ERCOT issued an OCN for capacity shortage for hours 21:00 and 22:00. |
| 3/31/08 | 9:30 | 10:15 | ERCOT issued an Alert for capacity shortage for hours 19:00 through 24:00. |
| 3/31/08 | 13:00 | 22:31 | Advisory ARR below 3000 MW. |

Transmission

3/17	Emergency Notice issued for the Rio Grande Valley.  Loss of the North Edinburg – Lon Hill 345KV would cause voltage collapse in area.

3/19  	Transmission Alert issued for loss of Sandow - Austrop double circuit causes low voltage and possible voltage collapse in Milano/Minerva Area.

Other

3/13 	Held the 00:15 interval, resumed at 00:45 due to congestion management tool input error.

3/13 	Held interval 09:30 real-time balancing deployments and resumed with interval 10:15.

3/14  	Held interval 04:15 deployments and resumed with 04:45 due to an incorrect zonal constraint value being entered.

Texas RE Event Analysis

3/10     23:24	Matador SPS armed and actuated at Whirlwind Energy Center.

3/10     23:41	Matador SPS armed and actuated at Whirlwind Energy Center.

3/13	13:43	Stanton East Wind SPS armed and actuated.

3/16	11:38	NERC Disturbance Control Standard (DCS) Event and under

frequency deviation (0.3 Hz)

3/18     16:27	138 kV bus, 345/138 kV Autotransformer and Unit with 634 MW tripped offline in Central Texas.

3/19 	11:38	Two RMR Units forced offline due to reported grass fire in the area.

3/21	11:33	Stanton East Wind SPS armed and actuated.