| NOGRR Number | 020 | NOGRR Title | Synchronization of OGRR198, Firm Load Shed Implementation Time Periods |
| --- | --- | --- | --- |
| Date Posted |  | April 16, 2008 |  |

| Nodal Operating Guide Section Requiring Revision | 4.5.3, Implementation |
| --- | --- |
| Protocol Section(s) Requiring Revision, if any | N/A |
| Requested Resolution | Normal |
| Revision Description | This Nodal Operating Revision Request (NOGRR) incorporates relevant language from OGRR198 which was approved by TAC on 03/06/08. |
| Reason for Revision | To incorporate into the Nodal Operating Guides provisions approved by TAC for the Zonal market and determined by the ERCOT stakeholders to be relevant to the Nodal market. |
| Overall Market Benefit | This NOGRR will result in a nodal market design that more completely reflects the intentions of the ERCOT stakeholders. |
| Overall Market Impact | None. |
| Consumer Impact | None. |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Inclusion of these revisions provides for a Nodal market design that more completely reflects the intentions of the ERCOT stakeholders. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Jonte on behalf of the Operating Guides Revision Task Force (OGRTF) |
| E-mail Address | John.jonte@CenterPointEnergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2252 |
| Cell Number |  |
| Market Segment | IOU |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Ann Boren |
| E-Mail Address | aboren@ercot.com |
| Phone Number | 512-275-7411 |

Proposed Guide Language Revision

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EECP steps below, notifying all Qualified Scheduling Entities (QSEs) and TOs, and coordinating the implementation of the EECP Conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants (MPs)they represent of each declared EECP step.

(2)	ERCOT has the authority to obtain emergency assistance energy over the Direct Current Tie(s) (DC Tie) for use by ERCOT.  ERCOT is also the coordinating authority for requests for emergency type power into or out of ERCOT.

(3) 	ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all steps in sequence.  ERCOT can immediately implement Step 4 of the EECP any time the system frequency is below 59.8 Hz and will immediately implement Step 4 any time the frequency is below 59.5 Hz.

(5)	Percentages for Step 4 Load shedding will be based on the previous year's TSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EECP steps to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that Step (and all above if not previously accomplished) and if ordered by the ERCOT Shift Supervisor or his designate, shall report back to the ERCOT System Operator when the requested step has been completed.

(7)	During EECP Step 4, ERCOT must be capable of shedding sufficient firm load to arrest frequency decay and to prevent generator tripping.  The amount of firm load to be shed may vary depending on ERCOT grid conditions during the event. Each TSP will be capable of shedding their allocation of firm load, without delay.  The maximum time for the TSP to interrupt firm load will depend on how much load is to be shed and whether the load is to be interrupted by SCADA or by the dispatch of personnel to substations.  Since the need for firm load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed 30 minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed load will be implemented within a time period not to exceed one hour;

(c)	The initial clock on the firm load shed shall apply only to load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first load shed instruction, ERCOT determines that an additional amount of firm load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

(8)	Each TSP, or its Designated Agent, will provide ERCOT a status report of load shed progress within 30 minutes of the time of ERCOT’s instruction or upon ERCOT’s request.