ERCOT Operating Guides

Section 3:  Operational Interfaces

QSE and TDSP Interface with ERCOT

May 1, 2008

Contents

3.	Operational Interfaces	3-4

3.1	System Control Interfaces with ERCOT	3-4

3.1.1	Introduction	3-4

3.1.2	Compliance with Dispatch Instructions	3-4

3.1.3	Qualified Scheduling Entities	3-6

3.1.4	Power Generation Companies	3-10

3.1.5	Transmission and/or Distribution Service Providers	3-21

3.1.6	Responsibility For Equipment Ratings	3-25

3.2	Scheduling Interfaces with ERCOT	3-26

3.2.1	Scheduling-Related Duties of Qualified Scheduling Entities	3-26

3.2.2	Scheduling Process	3-28

3.2.3	Procurement of Replacement Reserve Service Resources	3-29

3.2.4	Procurement of Additional Ancillary Services	3-30

3.2.5	Direct Current Tie Interconnection Day Ahead Scheduling Process	3-30

3.2.6	Dynamic Schedules	3-30

3.2.7	Approval of the Use of Responsibility Transfer (RspT) Schedules	3-32

3.3	Document Control	3-34

Protocol References

Reference:  Protocol Section 5.4.4, Compliance with Dispatch Instructions	3-4

Reference:  Protocol Section 4.3.4, Operations of the Qualified Scheduling Entity	3-6

Reference:  Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision	3-7

Reference:  Protocol Section 4.4.15, QSE Resource Plans	3-9

Reference:  Protocol Section 5.5.1, Changes in Resource Status (In Part)	3-9

Reference:  Protocol Section 5.5.1, Changes in Resource Status (In Part)	3-10

Reference:  Protocol Section 6.10.2, General Capacity Testing Requirements (In Part)	3-13

Reference:  Protocol, Section 6.10.3.5, Reactive Supply from Generation Resources required to provide VSS	3-15

Reference:  Protocol Section 5.5.2, Changes in Transmission Facility Status	3-21

Reference:  Protocol Section 6.4.2, Determination of ERCOT Control Area Requirements (In Part)	3-21

Reference:  Protocol  6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability (In Part)	3-22

Reference:  Protocol  6.5.7.2, QSE Responsibilities (In Part)	3-22

Reference:  Protocol  Section 6.5.7.3, ERCOT Responsibilities (In Part)	3-22

Reference:  Protocol Section 6.7.6,  Deployment of Voltage Support Service (In Part)	3-22

Reference:  Protocol Section 4.3.2, Schedule Components	3-26

Reference:  Protocol Section 4.3.3, Special Scheduling Considerations for Split Generation Meters	3-27

Reference:  Protocol Section 4.3.4, Operations of the Qualified Scheduling Entity	3-27

Reference:  Protocol Section 4.3.5, Requirement for Balanced Schedules (In Part)	3-28

Reference:  Extracted from Protocol Section 4.1.1 and Operating Guides Section 2.5.1	3-28

Reference: Protocol Section 4.1.2, Adjustment Period Scheduling Process (In Part)	3-29

Reference:  Protocol Section 4.4.18.4, Settlement (In Part)	3-30

Reference:  Protocol Section 4.9.1, Dynamic Load Schedules	3-30

Reference:  Protocol Section 4.9.2, Approval of the Use of Dynamic Load Schedules	3-31

Reference:  Protocol Section   4.9.3, Principles for Dynamic Schedules	3-31

Reference:  Protocol Section 4.9.4.1, Approval of the Use of Responsibility Transfers	3-32

Reference:  Protocol Section 4.9.4.2, Principles for Responsibility Transfers	3-32

Reference:  Protocol Section 4.9.5, Responsibility Transfer for Balancing Energy Bidding	3-33

# Operational Interfaces

## 3.1	System Control Interfaces with ERCOT

### 3.1.1	Introduction

ERCOT Control Area Authority, the Control Area Operator (CAO) of the ERCOT System, is authorized to take specific actions for the purpose of securely operating the ERCOT Transmission Grid in conformance with the standards specified in Protocol Section 5.2, North American Electric Reliability Corporation/ERCOT Tagging Procedures.

The following sections define the specific interface between Qualified Scheduling Entities and Transmission and/or Distribution Service Providers to allow the Control Area Authority to ensure the security and reliability of the ERCOT System, under normal operations.  Emergency operation is fully described in Part 4 of this Guide.  PGCs can communicate directly with ERCOT Control Area Authority under emergency and specific scheduling activities.

All other Entities operating in the ERCOT System interface either to the Qualified Scheduling Entities or the Transmission and/or Distribution Service Providers.

### 3.1.2	Compliance with Dispatch Instructions

Reference:  Protocol Section 5.4.4, Compliance with Dispatch Instructions

- Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions, unless in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols.

- If the recipient of a valid Dispatch Instruction does not comply because in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols, then, the TDSP or QSE must immediately notify ERCOT and provide the reason for non-compliance.

- If the recipient of a Dispatch Instruction recognizes that the Dispatch Instruction conflicts with other valid instructions or is invalid, the recipient will immediately notify ERCOT of the conflict and request resolution.

- Upon receipt of notice of non-compliance or conflict with Dispatch Instructions, ERCOT may, but is not required to, issue new Dispatch Instructions in response to the TDSP or QSE’s notice.

- ERCOT’s final instruction in effect will apply for all Protocol-related processes. If the QSE does not comply after receiving the final instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

- ERCOT’s final instruction to a TDSP in effect will apply for all Protocol-related processes. If the TDSP does not comply after receiving the final instruction, the TDSP shall remain liable for such failure under these Protocols in accordance with the TDSP’s Agreement with ERCOT.

- In all cases in which compliance with a Dispatch Instruction is disputed, both ERCOT and the QSE or TDSP shall document their communications, agreements, disagreements, and reasons for their actions, to enable resolution of the dispute through the ADR process in Section 20, Alternative Dispute Resolution.

Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions.

The TDSP or QSE shall immediately notify ERCOT if the recipient of a valid Dispatch Instruction does not comply.  The TDSP or QSE shall provide the reason for non-compliance in one of the following categories:

- Threat to safety,

- Risk of bodily harm,

- Damage to the equipment, or

- Not in compliance with the Protocols.

A recipient of a Dispatch Instruction shall immediately notify ERCOT Control Area Authority of any conflicts within acceptable limits and request resolution.  Conflicts within acceptable limits are:

- The Dispatch Instruction conflicts with other valid instructions, or

- The Dispatch Instruction is invalid.

ERCOT Control Area Authority may, but is not required to, alter or retract Dispatch Instructions in response to the TDSP or QSE’s notice of conflict.

ERCOT Control Area Authority’s final Dispatch Instruction in effect to a QSE shall apply. If the QSE does not comply after receiving the final Dispatch Instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

ERCOT Control Area Authority’s final Dispatch Instruction to a TDSP in effect shall apply. If the TDSP does not comply after receiving the final Dispatch Instruction, the TDSP shall remain liable for such failure in accordance with the TDSP’s Agreement with ERCOT.

ERCOT and the QSE or TDSP shall document the following information in the case of a dispute over compliance with a Dispatch Instruction:

- Communications,

- Agreements,

- Disagreements, and

- Reasons for their actions.

Documentation shall be retained for a minimum of 3years or until the related dispute is resolved.

Each QSE, or their agent shall immediately forward any valid Dispatch Instruction to the appropriate Resource or group of Resources.

### 3.1.3	Qualified Scheduling Entities

#### 3.1.3.1	Operating Obligations

Reference:  Protocol Section 4.3.4, Operations of the Qualified Scheduling Entity

Scheduling Center Requirement.  A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.

QSE Representative.  Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate a representative who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.  Each QSE shall provide the ERCOT Control Area Authority (CAA) with its written backup control plan to continue operation in the event the QSE’s scheduling center becomes inoperable.

Each backup control plan shall be reviewed and updated annually and shall meet the following minimum requirements:

- Description of actions to be taken by QSE personnel to avoid placing a prolonged burden on ERCOT and other Market Participants.

- Description of specific functions and responsibilities to be performed to continue operations from an alternate location.

- Includes procedures and responsibilities for maintaining basic voice communications capabilities with ERCOT.

- Includes procedures for backup control function testing and the training of personnel.

As an option, the backup control plan may include arrangements made with another entity to provide the minimum backup control functions in the event the QSE’s primary functions are interrupted.

Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate an individual who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

For connectivity requirements for backup sites, refer to Section 8.3.1.1, QSE Use of Domain Name Service (DNS) or ERCOT Web-Based Front Page for Site Failover.

Reference:  Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision

Operating Period data will be used by ERCOT to monitor the reliability of the ERCOT System in Real Time, monitor compliance with Ancillary Service Obligations, perform historical analysis, and predict the short-term reliability of the ERCOT System using network analysis software.  Each TDSP, at its own expense, may obtain such Operating Period data from ERCOT or from QSEs.

(1)	A QSE representing a Generation Entity that has Generation Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit at a Generation Resource plant location and ERCOT will make the data available to the Generation Resource’s host TDSP (at TDSP expense):

(a)	Gross and net real power, or

Gross real power at the generator terminal and unit auxiliary load real power, or

Net real power at the EPS meter and unit auxiliary load real power.

(b)	Gross reactive power at the generator terminal

(c)	Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System;

(d)	Frequency Bias of Portfolio Generation Resources under QSE operation;

(e)	Any data mutually agreed by ERCOT and the QSE to adequately manage system reliability and monitor Ancillary Service Obligations;

(f)	Generator breaker status;

(g)	High Operating Limit; and

(h)	Low Operating Limit.

[PRR590: Add items (i) and (j) upon system implementation:] (i) AGC status; and (j) Ramp rate.

[PRR307: Revise Section 6.5.1.1(1) and 6.5.1.1(1)(f) as follows when system change implemented.] (1) A QSE representing a Generation Entity or a Competitive Retailer that has Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit or LaaR capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) at a Resource plant location and ERCOT will make the data available to the Resource’s host TDSP (at TDSP expense): (f) Resource breaker status;

[PRR590: Add paragraph (2) and renumber subsequent paragraphs upon system implementation:] (2) A QSE representing Uncontrollable Renewable Resources is exempt from the requirements of Section 6.5.1.1(1)(i) and (j).

(2)	Any QSE providing Responsive Reserve and/or Regulation must provide for communications equipment to receive ERCOT telemetered control deployments of service power.

(3)	Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Resources.

(4)	Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using interruptible Load as a Resource shall provide separate telemetry of the real power consumption of each interruptible Load providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that interruptible Load.  If interruptible Load is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

(5)	Any QSE that represents a qualified provider of Balancing Up Load (BUL) need not provide telemetry but rather shall provide an estimate in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load.

(6)	Real Time data for reliability purposes must be accurate to within three percent (3%).  This telemetry may be provided from relaying accuracy instrumentation transformers.

[PRR590: Add paragraph (7) upon system implementation:] (7) A QSE representing a combined cycle plant may aggregate the AGC and ramp rate SCADA points for the individual units at a plant location into two distinct SCADA points (AGC and ramp rate) if the plant is configured to operate as such, i.e. gas turbine(s) and steam turbine(s) are controlled in aggregate from an AGC perspective.

#### 3.1.3.2	Daily Resource Plan

Reference:  Protocol Section 4.4.15, QSE Resource Plans

Each QSE that represents a Resource will present a Resource Plan to ERCOT at 1600.  These Resources may be specific Generation Resources and/or LaaRs.  The Resource Plan capacity should be sufficient to accommodate the combined quantity of energy and Ancillary Services scheduled by that QSE from the Resources that the QSE represents.  The Resource Plan shall indicate the availability of the Resources represented by the QSE, including a lead-time status code, and the planned operating level of each Resource, for each hour of the Operating Day.  The Resource Plan shall indicate the HOL and LOL, and HSL and LSL by Resource.  A Resource may be listed as unavailable to ERCOT if the Resource’s capacity has been committed to markets in regions outside of ERCOT.  ERCOT shall use other Resource Dispatch options to maintain system reliability prior to Dispatching a Generation Resource below its LOL.  ERCOT shall request Qualifying Facilities (QF), hydro units, and/or nuclear to operate below their LOL only after other Resource Dispatch options have been exhausted.

QSEs shall use best efforts, consistent with Good Utility Practice, to continually update their Resource Plans to reflect the current and anticipated operating conditions of the Resources.  ERCOT will monitor the performance of QSEs with respect to the submission of accurate Resource Plans in accordance with the measures established in Section 4.10, Resource Plan Performance Metrics.  ERCOT will work with individual QSEs as necessary to improve the individual QSE performance.

Reference:  Protocol Section 5.5.1, Changes in Resource Status (In Part)

The QSE will notify ERCOT of an unplanned change in Resource status as soon as practicable following the change. The QSE representing the Resource will report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status…

Each QSE that represents a Resource, either Load or Generation, shall submit to the ERCOT Control Area Authority by 1600 hours each day their Resource Plan for the next day.

The capacity of all Resources shown as available in the Resource Plan should be sufficient to accommodate the combined quantity of energy and Ancillary Services scheduled by that QSE from the Resources which the QSE represents.

The Resource Plan shall indicate the availability of all Resources represented by the QSE and the planned operating level of each Resource, for each hour of the Operating Day.

The Resource Plan shall indicate the High Operating Limit and Low Operating Limit of each Resource.

A Resource may be listed as unavailable to ERCOT if the Resource’s capacity has been committed to markets in regions outside of ERCOT.

The QSE representing the Resource will report to ERCOT any changes in Resource status by updating its Resource Plan before the beginning of the next hour following the change in status

#### 3.1.3.3	Unplanned Load Changes

Reference:  Protocol Section 5.5.1, Changes in Resource Status (In Part)

The QSE will notify ERCOT of an unplanned change in Resource status as soon as practicable following the change. The QSE representing the Resource will report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status…

The QSE shall notify ERCOT Control Area Authority of an unplanned change in load resource status as soon as practical following the event.

The QSE representing the load that is to be used as a resource shall provide ERCOT Control Area Authority with an update of the load status.  The update will be provided in the Resource Plan by the beginning of the next hour following the change in status.

Each QSE shall call on resources from which commitments have been made to provide Ancillary Services.

#### 3.1.3.4	QSE Responsibility for Department of Energy (DOE) and NERC Reportable Events

QSEs shall provide ERCOT with the DOE Form OE-417 report for each DOE reportable event that happens in areas they represent.  ERCOT, as the Control Area Authority, will forward these reports to the DOE and NERC as required.

### 3.1.4	Power Generation Companies

This Section defines the minimum requirements for the integration of generation facilities greater than 10 MW into the ERCOT System.

A generation facility shall be defined as any individual generating unit at a plant location that supplies energy to the ERCOT System.

Each generation facility shall meet the following general requirements in order to integrate into the ERCOT System.

- Physically located in the ERCOT Control Area,

- Represented by a QSE represented PGC, or directly by a QSE.

A QSE shall be the reporting Entity for a PGC and shall communicate with both ERCOT Control Area Authority and the TDSP maintaining the PGCs connection.

The QSE reporting for a PGC or a generation facility shall provide the following telemeter quantities for generation facilities greater than 10 MW to ERCOT Control Area Authority:

- Generator megawatts,

- Generator megavars,

- Generator energy (megawatt-hours),

- Substation equipment status, and

- Voltage where the facility connects to the Transmission Grid

- The directly connected TDSP may obtain any required data from ERCOT.

These quantities are fully described in Operating Guide 2.

The PGCs reporting QSE shall provide a separate, dedicated and reliable communications voice channel to each of ERCOT Control Area Authority and the directly connected TDSP and reliable data communications to both ERCOT Control Area Authority and the directly-connected TDSP.

The PGCs reporting QSE shall, as a minimum, provide adequate modeling information, as follows:

- Machine impedance and characteristics,

- Excitation system data, governor system constants,

- Transformer impedance, and

- Other relevant information.

This information is necessary to support ERCOT and TDSP’s ability to perform operational and planning studies such as:

- Transient and Dynamic Stability

- Short Circuit

- Load Flow

- Reliability Evaluations

When in operation, the generation facility greater than 10 MW shall be staffed or monitored 24 hours per day, by personnel capable of making operating decisions and possessing the ability to control the generation facility output when requested by the representing QSE or the directly connected TDSP during Black Start procedures.

The generation facility shall perform maintenance, start-up, and operation in a reliable and safe manner consistent with Good Utility Practices.

The generation facility shall implement the following in a reliable and safe manner and in accordance with the switching procedure of the directly connected TDSP:

- Synchronizing of the generation to the ERCOT System,

- Transmission switchyard switching or clearances.

The operation of a generation facility shall conform to the requirements of ERCOT or NERC Operating Criteria, Guide, or Standard.

The generating facility licensed by a federal regulatory agency shall, through its QSE representative, provide any applicable grid interconnection and performance licensing requirements to ERCOT and the TDSP to which the licensee is connected.

The TDSP is obligated to incorporate any such licensing requirements into its planning and operations, and the ERCOT Control Area authority shall support such requirements. Both ERCOT and the TDSP will create necessary procedures for satisfying these requirements. Such procedures will include provisions to notify the facility licensee through its QSE of any requirements that cannot be satisfied.

Any proposal for revision of this Operating Guide and the procedures incorporating the licensee requirements that would diminish the obligation or ability of ERCOT or the TDSP to support these requirements shall be provided to the licensee through its QSE to afford it an opportunity for review and response. Any such proposal that is approved, as a result of which the licensee is required to implement changes to meet its license requirements or to seek amendment to its license, shall become effective no sooner than 6 months following the approval.

#### 3.1.4.1	PGC Data Reporting

The PGC’s reporting QSE shall provide the following information to ERCOT Control Area Authority at the times specified:

| TIME | INFORMATION |
| --- | --- |
| Every 10 seconds | - Generation net MW output - Generation net MVAR - Status of switching devices in switchyard - Generating unit breaker status - Generating unit High Operating Limit - Generating unit Low Operating Limit |
| Daily | - Planned unit status, - Planned unit capability (both hourly and daily), - Fuel limitations. The reporting Entity will promptly report this condition to ERCOT Control Area Authority |
| Annually | - Seasonal capability where applicable, - Planned maintenance schedules. This information shall be updated when it changes. |
| Upon request | - Fuel capability as described in Section 6.2.7, Unit Alternative Fuel Capability Operating Guide Form, in conjunction with an Operating Condition Notice, Alert, Advisory, or Emergency Notice, |

Each generator at a generation facility shall have its turbine’s automatic speed governor in service when the generator is   in normal operation.  Testing and regulation performance of the speed governor shall be in accordance with Section 2.2.5, Turbine Speed Governors, of these Operating Guides.  The generator operator is required to notify the ERCOT Control Area Authority, through its QSE, if the operation of speed governors is impaired.

Each generation facility providing an Ancillary Service shall provide output consistent with the requirements of that Ancillary Service and ERCOT instructions.

In the event of an ERCOT declared Emergency, ERCOT may require the QSE to notify the generation facility through the reporting Entity and require it to increase or decrease generation or change voltage and reactive requirements in accordance with the Protocols.  The generation facility shall use its best efforts in meeting these required output levels in order that the ERCOT System can maintain safe and reliable operation.

It is the responsibility of all generators to carry an operational share of reactive support to insure adequate and safe Voltage Profiles are maintained in all areas of ERCOT.  To accomplish this, the following requirements shall apply to each generation facility.

- Each generation facility shall have Automatic Voltage Regulators and power system stabilizers in service as defined in Section 3.1.4.5, Automatic Voltage Regulators and Power System Stabilizers, below.

- The generation facility shall be designed and operated consistent with its obligations to supply Voltage Support Service as required in the ERCOT Protocols and ERCOT Control Area Authority Procedures.

- ERCOT has the right and obligation to Dispatch the reactive output (Vars) of each generation facility within its design capability to maintain adequate transmission voltage in ERCOT.

- ERCOT and the TSP shall be notified of any equipment changes that affect the reactive capability of an operating generating unit no less than 60 days prior to implementation of the changes, and any such changes that decrease the reactive capability of the generating unit below the required level must be approved by ERCOT prior to implementation.

- High reactive loading or reactive oscillations on generation units should be communicated to the QSE, the transmission operator, and ERCOT as soon as practicable.

- The tripping off line of a generating unit due to voltage or reactive problems should be reported to ERCOT, the transmission operator, and the QSE as soon as practicable.

Reference:  Protocol Section 6.10.2, General Capacity Testing Requirements (In Part)

QSEs shall provide ERCOT a list identifying each Generation Resource unit that is expected to operate more than one hundred sixty eight (168) hours in a Season as a provider of energy and/or Ancillary Services.  ERCOT shall evaluate, during each Season of expected operation, the Net Dependable Capability of each unit expected to operate more than one hundred sixty eight (168) hours during that Season, except for any Generation Resources used solely for energy services and whose capacity is less than ten (10) MW.  Prior to the beginning of each Season, QSEs shall identify the Generation Resources to be tested during the Season and the specific week of the test if known.  This schedule may be modified by the QSE (including retests) during the Season.  QSEs not identifying a specific week for a Generation Resource unit test must test the unit within the first one hundred sixty eight (168) hours of run time during the Season or operate with a Net Dependable Capability equal to the highest integrated hourly MWh output demonstrated during the first one hundred sixty eight (168) hours of run time.  QSEs do not have to bring units On-line or shut down solely for the purpose of the seasonal verification.  Any unit for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing services using the Generation Resource unit even if it fits the less than one hundred sixty eight (168) hour or small capacity exception.  The capability of hydro units operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall be evaluated by Season.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement…

#### 3.1.4.2	Enforcement Of Unit Capability Testing Requirement

In the event that a QSE fails to meet the Protocol requirements requiring seasonal unit capability testing, ERCOT shall provide this QSE with notice of its failure to meet the Protocols.  This notice shall be sent to the primary contact of the QSE representing the generating unit via both EMAIL and surface mail.  In addition to this written notice ERCOT shall make a reasonable effort to notify the QSE via telephone.

ERCOT shall allow the QSE three (3) days to correct the omission by submitting the ERCOT approved test results as required by these guides.   If the generating unit in question is operated during these three days, and no test results are provided to ERCOT, then the QSE shall be disqualified from provision of Ancillary Services.

If the generating unit is not operated and included in a QSE Resource Plan after the notification of the protocols violation, then ERCOT shall not disqualify the A/S provider unless/until the unit is operated and included in a Resource Plan that might be depended upon for Ancillary Services.

#### 3.1.4.3	Unit Reactive Capability Testing

Reference:  Protocol, Section 6.10.3.5, Reactive Supply from Generation Resources required to provide VSS

(1)	The Generation Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources required to provide VSS, as required by the Operating Guides.  Generation Resources required to provide VSS reactive capability limits shall be specified considering nominal substation voltage.

(2)	The Generation Entity will conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests will be performed on initial qualification and at a minimum of once every two years ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Generation Entity is not obligated to place Generation Resources required to provide VSS On-line solely for testing.  The reactive capability tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

(3)	Maximum lagging power factor reactive operating limit shall be demonstrated during peak Load Season, at or above ninety-five percent (95%) of the most currently tested net dependable megawatt capability, insofar as system voltage conditions and other factors will allow.  The Generation Resource required to provide VSS should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

(4)	Maximum leading power factor reactive operating limit shall be demonstrated during light Load conditions, with the unit operating at a typical output for that condition, insofar as system voltage conditions and other factors will allow.  The unit should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

(5)	The Generation Entity shall perform the unit Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every five (5) years.  The AVR tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

##### 3.1.4.3.1	Corrected Unit Reactive Limits (CURL)

The reactive capability curve for each unit on the ERCOT System shall be submitted to ERCOT containing the most limiting elements for the leading and lagging reactive output. The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing may be produced on the corrected reactive capability curve. The corrected reactive capability curve establishes the CURL at the unit terminals that ERCOT Planning and ERCOT Operations will use for their studies. ERCOT Operations, after reviewing the updated curves and checking them for reasonableness, will forward copies to the Steady State Working Group, for use in modeling such capability in the ERCOT transmission planning cases. If ERCOT finds the submitted CURL unreasonable, ERCOT will follow the “ERCOT Implementation” section of this procedure. The reactive capability represented in the CURL will be used in operation and planning studies.  For all intents and purposes this new curve would take the place of the original manufacturer’s unit reactive capability curve.

##### 3.1.4.3.2	Non-Coordinated Testing

The QSE representing the generating unit shall give ERCOT at least two hours advance notice prior to the start of the test.  ERCOT retains the right to cancel the reactive test if ERCOT believes, in its sole judgment, that conducting the test at the requested time could jeopardize the reliability of the ERCOT System.  For example, ERCOT can cancel a requested leading capability test during a time when system voltages are low or expected to be low due to factors such as high import power levels, transmission line outages, capacitor bank outages, or generating unit outages or exciter limitations.

Tests to verify maximum lagging reactive capability shall be conducted during times when ERCOT System Loads are high, such as summer season afternoons when ambient temperatures exceed 90F, but not necessarily at the time of system peak.  Units being tested shall be operating at or above 95% of net dependable real power (MW) output.

Tests to verify maximum leading reactive capability shall be conducted during times when ERCOT System Loads are low, such as off-peak hours during the spring season.  Units being tested shall be operating at a real power (MW) output representative of its usual loading during such light Load periods.

The PGC shall measure the tested reactive capability at the generator terminals minus the auxiliary reactive consumption.  Additionally, the tested reactive capability shall be measured at the high side of the generator step up transformer if metering is available. If metering is not available at the high side, the PGC shall calculate the reactive capability at the high side using the method specified in the appendix of the Biennial Unit Reactive Limits (Lead and Lag) Verification form located in Section 6.2.3, Biennial Unit Reactive Limits (Lead and Lag) Verification.  Both high side and generator terminal values are required on the form for proper submittal of the test results.

The QSE representing a generating unit shall be responsible for scheduling reactive verification Tests in accordance with the conditions outlined above.

ERCOT shall have the option to waive the requirement to test and verify the maximum leading reactive capability of any generating unit that seldom runs during such light Load periods.  The granting of such a waiver is at ERCOT’s sole discretion, and any such waiver shall be effective for two years.

The minimum duration for any reactive verification test, leading or lagging, is fifteen minutes.  The corrected curves (“CURL”) should be posted in the PGC’s control room, where the tests are conducted, at the QSE’s Real Time/generation dispatch desk, and copies should be provided to ERCOT Operations. During any test, the unit must maintain its generator cooling system at normal operating level.  Tests will be conducted to produce MVARs at a level not less than 90% of the amount indicated by the existing reactive capability curve (original manufacturer’s unit reactive capability curve, or the most recent CURL).

The QSE representing a generating unit shall be responsible for the timely and accurate reporting of test results to ERCOT.  The QSE representing a generating unit shall be responsible for the timely submittal to ERCOT of an updated CURL reflecting any known changes in the reactive output of the unit.  All required data fields on the Biennial Unit Reactive Limits (Lead and Lag) Verification form must be properly completed for a valid test to be considered valid.

##### 3.1.4.3.3	Coordinated Testing

Coordinated Testing is the testing of a generator’s reactive capability to verify the generating unit’s most current CURL. The verification test will be a coordinated effort between the PGC, the PGC’s QSE, the TO which the PGC is connected, and ERCOT Operations.  Coordinated Testing is at the option of the PGC or can be ordered by ERCOT if a retest is required for an established non-valid test performed using the NCTP.

The PGC requesting to perform a coordinated test will provide ERCOT Operations Engineering Support and the TO with a minimum of 48 hours notice of the proposed test date. Requests shall be made weekdays between 8 AM to 5 PM excluding recognized ERCOT holidays.  Upon receipt of a request for test, ERCOT Operations Engineering Support and the TO will evaluate the expected conditions and determine whether transmission system conditions conducive to a valid test can be created through coordinated network switching, modification of the generation reactive Dispatch of nearby generating units, or by some other means.  Having established that suitable transmission system conditions exist or can be created, ERCOT Operations Engineering Support and the TO shall provide the PGC and the QSE a concurrence of the test time and date or a rejection of the test time and date within 24 hours of the receipt of the request.

The coordinated test shall begin and end within the ERCOT Operations Engineer’s standard work day (nominally 8 AM to 5 PM).  Since leading tests will often occur in off-peak periods, the coordinated leading test shall begin and end at times agreed upon by ERCOT, the TO, QSE and PGC. The minimum duration for any reactive verification test, leading or lagging, is fifteen minutes.  The corrected curves (“CURL”) should be posted in the PGC’s control room, where the tests are conducted, at the QSE’s Real Time/generation Dispatch desk, and copies should be provided to ERCOT Operations. The testing period shall be scheduled such that adequate time is given for any transmission switching that may be performed to accommodate adequate system conditions for the appropriate reactive test. During the test, the QSE Operator shall be in communication with the TO in order to coordinate the reactive output of adjacent units, capacitor switching, reactor switching, and any other activity needed to perform the scheduled reactive test accurately.

LAGGING REACTIVE TESTS

Generating units shall be tested to verify lagging reactive capability at or above 95% of net dependable real power (MW) output as indicated on the CURL. It is during times when ERCOT System Loads are high and transmission system voltages are relatively low (such as summer season afternoons when ambient temperatures exceed 90F) that maximum lagging capability is most likely to be needed.  The transmission voltage at the switchyard to which the generating unit is connected should be at or below the ERCOT currently scheduled voltage prior to starting the test. All efforts should be made to maintain the ERCOT Voltage Profile during the test, but this may be varied at ERCOT’s discretion.

LEADING REACTIVE TESTS

Generating units shall be tested to verify leading reactive capability at a MW loading level representative of expected generating unit MW loading during minimum Load conditions as indicated on the CURL.  It is during times when ERCOT System Loads are light and transmission system voltages are relatively high (such as off-peak hours during the spring season) that maximum leading capability is most likely to be needed.  The transmission voltage at the switchyard to which the generating unit is connected should be at or above the ERCOT currently scheduled voltage prior to starting the test.  All efforts should be made to maintain the ERCOT Voltage Profile during the test, but this may be varied at ERCOT’s discretion.  At ERCOT’s sole discretion, the requirement to test leading capability may be waived for peaking generating units which seldom, if ever, run during light Load conditions.

The PGC shall measure the tested reactive capability at the generator terminals.  The reading recorded shall represent the net MVAR output of the generator and shall have the unit’s auxiliary reactive consumption deducted from the generator’s gross reactive output at the machine’s terminals.  Additionally, the tested reactive capability shall be measured at the high side of the generator step up transformer if metering is available.  If metering is not available at the high side, the PGC shall calculate the reactive capability at the high side using the method specified in the appendix of the Biennial Unit Reactive Limits (Lead and Lag) Verification form located in Section 6.2.3.  Both high side and generator terminal values are required on the form for proper submittal of the test results.

The QSE representing a generating unit shall be responsible for scheduling reactive tests in accordance with the conditions outlined above, and for the timely and accurate reporting of test results to ERCOT.  All test documents shall be submitted by the PGC’s QSE.  All required data fields on the Biennial Unit Reactive Limits (Lead and Lag) Verification form must be present for a valid test.

##### 3.1.4.3.4	ERCOT Implementation

Reactive test results shall be reviewed by ERCOT staff to determine the accuracy and consistency of the test data provided, and to determine the appropriateness of unit loading and system conditions during the test.  In the event of significant discrepancies, ERCOT shall have the right to order a re-test of the unit.

Reactive test results shall be reviewed by ERCOT staff to determine if test results fall within 90% of CURL expectation.  If test results are less than 90% of CURL expectation, ERCOT shall have the right to either order the PGC to produce a new CURL, or to order a re-test of the unit.

Reactive test results shall be reviewed by ERCOT staff against the most recent CURL for the unit.  If unit reactive capability appears to be inappropriately limited by unit controls or relays, ERCOT staff shall contact the PGC and attempt to resolve the discrepancy.  ERCOT shall have the right to order the PGC to produce a new CURL that reflects current operating limits.

CURL data validated by test, and any new CURL produced by a PGC in response to new operating limits, shall be implemented by ERCOT staff in its Operational Model within two weeks of receipt and resolution of the data.  As soon as practicable thereafter, ERCOT staff will provide such data to the ERCOT Steady State Working Group for implementation in the planning model.

##### 3.1.4.3.5	Enforcement of Unit Reactive Capability Testing

Details of the enforcement for reactive capability testing can be found in the Compliance Template located on the ERCOT Compliance Web Page.

#### 3.1.4.4	Enforcement Of AVR Testing

In the event that a QSE fails to meet the Protocol requirements requiring AVR testing, ERCOT shall provide this QSE with notice of its failure to meet the Protocols.  This notice shall be sent to the primary contact of the QSE representing the generating unit via both EMAIL and surface mail.  In addition to this written notice ERCOT shall make a reasonable effort to notify the QSE via telephone. ERCOT shall also provide notice directly to the primary contact for the Generation Resource Entity.

If a satisfactory reply, as determined by ERCOT, is not received from the Generation Entity, or its QSE within 30 days of their receipt of written notification, ERCOT shall notify the PUC Market Oversight Division of the Generation Resource Entity’s failure to comply with the Protocols.

#### 3.1.4.5	Automatic Voltage Regulators and Power System Stabilizers

Generator Automatic Voltage Regulators and power system stabilizers will be kept in service whenever possible.  Generation Entities shall notify their QSE, who in turn will promptly notify the ERCOT Control Area Authority by telephone of the circumstances, when a voltage regulator or stabilizer is unavailable due to maintenance or failure and when it is returned to normal operation.

Unit AVR and PSS modeling information required in the ERCOT Planning Criteria shall be determined from actual unit testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the TSP.

#### 3.1.4.6	Protective Relaying Requirement

The Facility’s generation machine characteristics and plant design shall incorporate the under-frequency firm Load shedding philosophy and criteria defined in Operating Guide 2.9. Requirements for Under-Frequency Relaying.  Inherent in this philosophy is the idea that all generators remain on line until all three steps of firm Load shedding have been executed.  In addition, Generation Resources must remain connected to the transmission system during the following operating conditions:

  - Generator terminal voltages are within five percent (5%) of the rated design voltage and volts per hertz are less than one hundred five percent (105%) of generator rated design voltage and frequency;

  - Generator terminal voltage deviations exceed five percent (5%) but are within ten percent (10%) of the rated design voltage and persist for less than 10.0 seconds;

  - Generator volts per hertz conditions are less than one hundred sixteen percent (116%) of generator rated design voltage and frequency and last for less than 1.5 seconds;

  - A transmission system fault (three-phase, single-phase or phase-to-phase), but not a generator bus fault, is cleared by the protection scheme coordinated between the Generation Entity and the TDSP on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in Protocol Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, item (7).  However, in the case of a generator bus fault or a primary transmission system relay failure, the generator protective relaying may clear the generator independent of the operation of any transmission protective relaying.

The generation Facility shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria as described in Section 5, Planning.

Within thirty (30) days of ERCOT’s request, Generation Resources shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Generating Resources required to provide VSS shall have and maintain the following capability:

(1)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least eighty percent (80%) of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(2)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment misoperation.

#### 3.1.4.7	Outages

Forced Outages

The Control Area Authority shall be advised via telemetry of all Forced Outages of ANY Resource capability within one minute.

Sabotage Information Exchange

A PGC or any ERCOT Entity shall inform the ERCOT operator when:

- It is suspected or identified that multi-site sabotage has occurred

- It is suspected or identified that a single-site sabotage of a critical facility has occurred

#### 3.1.4.8	Enforcement of Load acting as a Resource (LaaR) Testing Requirement

After initial qualification, a LaaR’s telemetry and any applicable relay functionality will be tested and validated by ERCOT within twenty-four (24) months as specified in these Operating Guides.  If a LaaR fails to provide the appropriate documents as required in the annual and biennial verification test for two (2) consecutive years, ERCOT shall notify the associated QSE of any noncompliance.  After a thirty (30) day allowance for the deficiency to be corrected, ERCOT shall reduce the Resource’s ability to provide Ancillary Services in the ERCOT market to zero.

### 3.1.5	Transmission and/or Distribution Service Providers

Reference:  Protocol Section 5.5.2, Changes in Transmission Facility Status

The TDSP will notify ERCOT of any changes in status of Transmission Facility elements as provided and clarified in the ERCOT procedures.  The TDSP will notify ERCOT of any other Transmission Facility status as soon as practicable following the change.  In addition, any short-term inability to meet minimum TSP or DSP reactive requirements shall be immediately reported to ERCOT by way of the TSP.

Reference:  Protocol Section 6.4.2, Determination of ERCOT Control Area Requirements (In Part)

…(6)	Voltage Support:  ERCOT in coordination with the TDSPs shall conduct studies to determine the normally desired Voltage Profile for all Voltage Support busses in the ERCOT System and shall post all Voltage Profiles on the Market Information System.  ERCOT may temporarily modify its requirements based on Current System Conditions.  ERCOT shall determine the amount of Voltage Support Service needed to provide sufficient reactive capacity in appropriate locations to provide ERCOT System security as specified in the Operating Guides…

Reference:  Protocol  6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability (In Part)

(1)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT.  This quantity of Reactive Power is the Unit Reactive Limit (URL).

(2)	Generation Resources required to provide VSS except as noted below in items (3) or (4), shall have and maintain a URL which has an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP…

Reference:  Protocol  6.5.7.2, QSE Responsibilities (In Part)

(1)	QSE Generation Resources required to provide VSS are expected to have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the Operating Guides…

…(5)	QSEs shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits…

Reference:  Protocol  Section 6.5.7.3, ERCOT Responsibilities (In Part)

(1)	ERCOT, in coordination with the TDSPs, shall establish, and update as necessary, Voltage Profiles at points of interconnection of Generation Resources required to provide VSS to maintain system voltages within established limits…

…(3)	ERCOT, in coordination with the TDSPs, shall deploy static Reactive Power Resources as required to continuously maintain dynamic Reactive Reserves from QSEs, both leading and lagging, adequate to meet ERCOT System requirements…

Reference:  Protocol Section 6.7.6,  Deployment of Voltage Support Service (In Part)

…(2)	ERCOT and TDSPs shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability…

ERCOT and TDSPs shall operate the ERCOT Interconnected System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures.

TDSPs monitoring system conditions shall notify ERCOT when Transmission Facility Elements reach safe operating limits as soon as practicable, if these Transmission Facility Elements will affect the ERCOT system.

A TDSP shall notify ERCOT Control Area Authority of any changes in their transmission facility status within 10 seconds of the change of status.

TDSPs shall follow ERCOT instructions related to ERCOT responsibilities:

- Performing the physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, protective relays, metering and load shedding equipment;

- Directing changes in the operation of transmission voltage control equipment;

- TDSPs will maintain voltage set points established by ERCOT utilizing static reactive devices.  TDSPs, under the direction of ERCOT, will coordinate TDSP static device switching with QSE dynamic reactive device operation.  Static reactive devices will be brought on line before predicted daily maximum load growth or dynamic reactive resources reach operating limits.  Static reactive devices will be taken off line during daily load decline and before dynamic reactive resources reach operating limits.  ERCOT will coordinate Automatic Voltage Regulator, dynamic and static reactive device outages to ensure adequate reactive reserves are maintained

- Taking those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT Transmission Grid to a secure state in the event of an ERCOT System Emergency.

Each TDSP, at its own expense, may obtain Operating Period data from ERCOT (See Section 2.3.1, Control Area Operator Authority).

#### Transmission Operator Responsibility for Department of Energy (DOE) and NERC Reportable Events

TOs shall provide ERCOT with the DOE Form OE-417 report for each DOE reportable event that happens in areas they represent.  ERCOT, as the Control Area Authority, will forward these reports to the DOE and NERC as required.

#### 3.1.5.2	Transmission Owner Responsibility for a Vegetation Management Program.

Each transmission owner shall have a Vegetation Management Program outlining procedures to prevent transmission line contact with vegetation.  The transmission owner shall maintain documentation to verify the performance of the Vegetation Management Program and shall provide that documentation to their respective Transmission Operator and ERCOT upon request.

Details of the NERC requirements can be found in the Vegetation Management Program Template located on the ERCOT Compliance Web Page.

#### 3.1.5.3	Outages

##### 3.1.5.3.1	NERC Requirements for Reporting Vegetation-Related Line Outages

In ERCOT, transmission owners shall report vegetation-related 345 kV transmission line outages for each calendar month to their respective Transmission Operator.  Transmission Operators shall report these monthly Outage statistics to ERCOT Compliance by the 20th of the following month.  ERCOT Compliance shall report results to NERC.

Details of the NERC requirements, including reporting exceptions, can be found in the Vegetation Management Program Template located on the ERCOT Compliance Web Page.

##### 3.1.5.3.2	ERCOT Requirements for Reporting Forced Outages

Forced outages of all transmission lines (>60 kV) shall be reported to ERCOT Control Area Authority immediately.

Forced outages of other transmission equipment that affect power flows or transfer capacity will be reported immediately to ERCOT Control Area Authority.

When a forced outage affects the overall security or capacity, ERCOT shall take remedial steps immediately to insure that other facilities are not loaded beyond capacity limits.

An Outage initiated by protective relay, or manually in response to an observation by field personnel or the TDSP System Operator that equipment poses a threat to personnel or equipment. The TDSP may remove such equipment from service immediately and notify ERCOT of its action.

##### 3.1.5.3.3	ERCOT Requirements for Reporting Scheduled Outages

When a transmission line (>60 kV) is out of service the capacity of ERCOT transmission lines should not be exceeded under normal or single contingency conditions.

TDSPs shall communicate the information to the Distribution Service Providers connected to that TDSP.

##### 3.1.5.3.4	ERCOT Requirements for Reporting Sabotage Information

A TDSP or any ERCOT entity shall inform the ERCOT operator when:

- It is suspected or identified that multi-site sabotage has occurred

- It is suspected or identified that a single-site sabotage of a critical facility has occurred.

- Occurred.

### 3.1.6	Responsibility For Equipment Ratings

TDSPs are responsible for determining the rating of their facilities.

Technical limits established for the operation of transmission equipment shall be applied consistently in TTC calculations, engineering studies, real-time security analyses, and operator actions.

TDSP’s shall provide ERCOT with three (3) nominal Transmission Facility Ratings:

- Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature.  The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

- Emergency Rating:  Represents the two (2) hour MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

- Fifteen Minute Rating:  Represents the fifteen (15) minute MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature and with a step increase from a prior loading of ninety percent (90%) of the Continuous Rating.  The Transmission Facility can operate at this rating for fifteen (15) minutes, assuming its pre-contingency loading was ninety percent (90%) of the Continuous Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

- In operating the Transmission Grid, ERCOT shall use these ratings as follows:

- ERCOT shall limit pre-contingency flows to enforce the Continuous Rating.

- If  a valid Remedial Action Plan  is unavailable to unload  the Transmission Facility post contingency or the pre-contingency loading is greater than ninety percent (90%) of the Continuous Rating, ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Continuous Rating within two (2) hours.

- If a Remedial Action Plan is documented at ERCOT to relieve the loading on the  Transmission Facility within fifteen (15) minutes; ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Fifteen Minute Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within fifteen (15) minutes.

- ERCOT shall use best efforts to restore all Transmission Facilities to within Continuous Ratings as soon as practicable, based on Good Utility Practice.

## 3.2	Scheduling Interfaces with ERCOT

### 3.2.1	Scheduling-Related Duties of Qualified Scheduling Entities

#### 3.2.1.1	Functions and Activities

QSEs must submit schedules that identify Obligations and Supply.  QSEs must submit Balanced Schedules for each Settlement Interval.  For a Schedule to be balanced total Energy Obligation must equal total Energy Supply and total Ancillary Services Obligation for each service type must meet total Ancillary Services Supply for each service type.

It is necessary to balance Ancillary Services schedules, as well as, Energy Schedules.  In order to do so, the QSE must indicate on its schedule the amount of Ancillary Services that will be purchased from the ERCOT Ancillary Services Market.

#### 3.2.1.2	Schedule Components

Reference:  Protocol Section 4.3.2, Schedule Components

Included in each Balanced Schedule is:

(1)	Energy to be produced by Resources that the QSE represents, by Congestion Zone;

(2)	Energy to be consumed by Loads that the QSE represents (including T&D Losses) by Congestion Zone;

(3)	ERCOT allocated Ancillary Services Obligations for the QSE;

(4)	Any energy and Ancillary Services scheduled to or from other QSEs (e.g. Inter-QSE Trades);

(5)	Any Balancing Energy scheduled through the ERCOT Scheduling Process; and

(6)	Any Self-Arranged Ancillary Services.

When relaxed Balanced Schedules are allowed by ERCOT, pursuant to Section 4.3.5, Requirement for Balanced Schedules, the requirement for subpart (2) above shall be relaxed and QSEs shall be allowed to schedule energy for Load that is equivalent to the amount of scheduled energy for Resources as specified in subpart (1) and (5) above.

Use of Balancing Energy scheduled via ERCOT to meet Obligations shall be limited to an amount supported by the QSE’s credit collateral with ERCOT.

#### 3.2.1.3	Special Scheduling Considerations for Split Generation Meters

Reference:  Protocol Section 4.3.3, Special Scheduling Considerations for Split Generation Meters

When a generation meter is split, as provided for in Section 10, Metering, two or more independent virtual generating units may be created for purposes of scheduling, ERCOT System operation, and settlement.

Each virtual generator unit may be scheduled by a different QSE.  A QSE may only schedule up to the fixed ownership percentage of the actual generator’s maximum output.

Each QSE will be responsible for including the virtual generator portion in its Resource Plan. A QSE’s Ancillary Services capacity will be bid for the jointly-owned unit on the basis of a fixed ownership percentage that is shown in the registration database.

ERCOT will handle scheduling discrepancies in the same manner as other units.

When a generation meter is split, as provided for in the Protocols, Section 10, Metering, two or more independent virtual generating units may be created for purposes of scheduling, ERCOT System operation, and settlement.

Each virtual generator unit may be scheduled by a different QSE.  A QSE may only schedule up to the fixed ownership percentage of the actual generator’s maximum output.

Each QSE will be responsible for including the virtual generator portion in its Resource Plan.

A QSE’s Ancillary Services capacity will be bid for the jointly owned unit on the basis of a fixed ownership percentage that is shown in the registration database.

ERCOT will handle scheduling discrepancies in the same manner as other units.

#### 3.2.1.4	Operations of the Qualified Scheduling Entity

Reference:  Protocol Section 4.3.4, Operations of the Qualified Scheduling Entity

Scheduling Center Requirement. A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.

QSE Representative. Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate a representative who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.

Each QSE shall, for the duration of the scheduling process and settlement period for which the QSE has submitted schedules to ERCOT, designate a representative who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

#### 3.2.1.5	Requirement for Balanced Schedules

Reference:  Protocol Section 4.3.5, Requirement for Balanced Schedules (In Part)

A QSE shall submit to ERCOT only Balanced Schedules, for both energy and Ancillary Services, in the Day Ahead Scheduling Process and the Adjustment Period. If a QSE submits a schedule that is not a Balanced Schedule, ERCOT shall reject that schedule in accordance with Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process…

A QSE shall submit to ERCOT only Balanced Schedules, for both energy and Ancillary Services, in the Day Ahead Scheduling Process and the Adjustment Period. If a QSE submits a schedule that is not a Balanced Schedule, ERCOT shall reject that schedule.

### 3.2.2	Scheduling Process

#### 3.2.2.1	Day Ahead Scheduling

Reference:  Extracted from Protocol Section 4.1.1 and Operating Guides Section 2.5.1

| DAY AHEAD TIME PERIOD | QUALIFIED SCHEDULING ENTITY (QSE) SUBMISSION: |
| --- | --- |
| 1100 | - Balanced Energy Schedule of Obligations and Resources - Self-Arranged AS Schedule |
| 1115 | - Resubmit corrected schedules |
| 1300 | - Update Balanced Energy Schedule of Obligations and Resources - Update Self-Arranged AS schedule - AS bids to supply AS to ERCOT AS Market |
| 1315 | - Resubmit corrected updated schedules. |
| 1500 | - Submit updated AS schedule that includes Self-Arranged and AS bids selected by ERCOT. |
| 1600 | - Submit Resource Plans with unit-specific information - Submit Replacement Reserve Service (RPRS) Bids and associated Balancing Energy bids. |
| After 1800 | - Modify RPRS bids |

#### 3.2.2.2	Adjustment Period Scheduling

Reference: Protocol Section 4.1.2, Adjustment Period Scheduling Process (In Part)

The Adjustment Period Scheduling Process will follow the following timeline with time T being the start of the Operating Hour:

| ADJUSTMENT PERIOD | QSE RESPONSIBILITY |
| --- | --- |
| Time = T minus 60 minutes | - Submit updated Balanced Schedule of Obligations and Supply for the hour beginning at Time T, and any hour after T. - Submit bids for Balancing Energy including any mandatory decremental Balancing Energy bids. - Submit updated Self-Arranged AS schedule for the hour beginning at Time T and any hour after Time T (the amount of Self-Arranged AS may not change from Day Ahead, however, the Resources supplying the Self Arranged AS may be altered. If ERCOT calls on additional AS in the AP, the allocated portion of the additional AS may be self- arranged). - Submit updates to Resource Plan. - Submit bids for RPRS. - Submit bids for additional Ancillary Services. - Submit bids for incremental and decremental Resource specific premiums. |
| Time = T minus 45 minutes | - Resubmit corrected schedules. |

### 3.2.3	Procurement of Replacement Reserve Service Resources

The typical RPRS procurement process will adhere to the following timeline:

| RPRS PROCUREMENT PROCESS | QSE RESPONSIBILITY |
| --- | --- |
| Time X | Submit or update bids for RPRS |
| Time X plus 60 minutes | Update Balanced Schedules |
| Time X plus 75 minutes | Resubmit corrected schedules. |

Time X is the start of a clock hour when ERCOT identifies Zonal and Local Congestion, or capacity insufficiency.

Time X can be the start of any clock hour during the Adjustment Period but cannot be less than 2 hours prior to the Operating Hour that energy from the RPRS unit is required.

RPRS bids remain active until withdrawn by the QSE.

### 3.2.4	Procurement of Additional Ancillary Services

The Adjustment Period AS procurement process for RRS, NSRS and RGS will use the following timeline with time X being the start of a clock hour when ERCOT identifies the need for additional AS.  Time X can be the start of any clock hour during the Adjustment Period but cannot be less than 2 hours prior to the Operating Hour that the additional AS capacity is required.

| ADDITIONAL AS PROCUREMENT PROCESS | QSE RESPONSIBILITY |
| --- | --- |
| Time X | Submit or update bids for RRS, NSRS and RGS |
| Time X plus 60 minutes | Update their Balanced Schedules, including additional Self-Arranged AS. Remove the portion of the bid, submitted by Time X, that are to be used in incremental self-arrangement and bilateral AS sales, if desired. |
| Time X plus 75 minutes | Resubmit corrected schedules. |

### 3.2.5	Direct Current Tie Interconnection Day Ahead Scheduling Process

Reference:  Protocol Section 4.4.18.4, Settlement (In Part)

A QSE exporting from ERCOT through a DC Tie export schedule will include that DC Tie export schedule as an Obligation in its Balanced Schedule by using the identifier field indicating the appropriate DC Tie.  Exports from ERCOT via DC Ties will be treated as a Load connected at transmission voltage in the settlement system and are responsible for allocated Ancillary Services, Transmission Losses, UFE, ERCOT administrative fees, as described in Section 9, Settlement and Billing, and any other applicable ERCOT fees…

A QSE exporting from ERCOT through a DC Tie export schedule will include that DC Tie export schedule as an Obligation in its Balanced Schedule.

A QSE importing into ERCOT through a DC Tie import schedule will include that DC Tie import schedule as a Supply in its Balanced Schedule.

### 3.2.6	Dynamic Schedules

Reference:  Protocol Section 4.9.1, Dynamic Load Schedules

QSE’s may use dynamic power signals to control generation to match a metered Load in order to minimize the QSE’s exposure to the Balancing Energy market. To implement the Dynamic Schedule the QSE will send Real Time telemetry to ERCOT that is equal to the metered Load, which the QSE wishes to follow.  ERCOT will integrate the signal for each Settlement Interval and provide the integrated signal to settlement as the scheduled Obligation for that metered Load. Settlement will use this integrated value as a scheduled Supply for that interval for the QSE. At settlement the integrated values will be used as a Supply or Obligation schedule.

The QSE’s schedule will include one Supply Resource (or fleet) designated to follow the Dynamic Schedule for a Load.  The designated Supply schedule will be estimated in the same manner as the designated Load.  At settlement, the estimated schedule for the designated Resource will be replaced with the integrated final power signal from the dynamic Load.

Reference:  Protocol Section 4.9.2, Approval of the Use of Dynamic Load Schedules

(1)	Each QSE desiring to use Dynamic Load Schedules must submit a proposal of the Dynamic Schedule to ERCOT for analysis of Congestion impacts and reliability in accordance with the Operating Guides.

(2)	Subject to number (1) above, any QSE representing Non Opt-In Entities that own, had under construction, or had contractual rights to Generation Resources, as of May 1, 2000, may use Dynamic Schedules.  Once a Non Opt-In Entity (NOIE) offers Customer Choice, it must submit a new proposal for Dynamic Load Scheduling to ERCOT.

(3)	ERCOT will approve dynamic scheduling proposals on a case-by-case basis.  Approval will be based on the schedule’s impact on ERCOT’s ability to determine and manage Congestion, ERCOT's ability to monitor Generation Resource and Load behavior associated with the schedule and the schedule’s impact on system reliability.  QSEs representing Non Opt-In Entities, which submit proposals in accordance with (1) and (2) above will be accepted by ERCOT.

(4)	New proposals for Dynamic Load Schedules within Congestion Zones will be considered after June 1, 2001 and across Congestion Zones after June 1, 2002.

Reference:  Protocol Section   4.9.3, Principles for Dynamic Schedules

(1)	All power signals for Dynamic Schedules must be sent to ERCOT in Real Time via telemetry.

(2)	Each Dynamic Load Schedule must be tied to a Load meter or group of Load meters.  This includes Load that is calculated by subtracting interchange telemetry from actual generation telemetry, appropriately adjusted for T&D Losses.  A Load or group of Loads that is/are dynamically scheduled can only be followed by Generation Resources represented by the same QSE as the Load.

(3)	Each Dynamic Load Schedule will indicate the dynamic power signal that will be used to create the final schedule.

(4)	Dynamic Load Schedules tied to Load meters (or groups of Load meters) may be used between Congestion Zones.

(5)	A QSE using Dynamic Load Schedules shall send a dynamic power signal or signals to ERCOT.

(6)	Each QSE with a Dynamic Load Schedule will include in its schedules and plans submitted to ERCOT, an estimate for the integration of the schedule for each Settlement Interval.  These schedule integration estimates will be used for allocation of RPRS costs.

(7)	ERCOT will integrate the dynamic power signal sent by a QSE for each Settlement Interval. This integrated signal shall replace the estimate and will be used in settlement as the final schedule. Dynamic Schedules do not alter the settlement process for metered Loads.

(8)	If a signal is lost for any reason, ERCOT will use the final schedule for Settlement purposes.

(9)	ERCOT will use the dynamic power signal in each of the applicable QSE’s SCE equation.

### 3.2.7	Approval of the Use of Responsibility Transfer (RspT) Schedules

Reference:  Protocol Section 4.9.4.1, Approval of the Use of Responsibility Transfers

(1)	Intra-zonal Responsibility Transfers (RspTs) will be approved unless ERCOT determines it cannot accommodate these transfers without compromising reliability or settlement accuracy.

(2)	Each QSE that proposes to use an RspT must submit a proposal of the RspT to ERCOT for analysis of Congestion impacts and reliability in accordance with the Operating Guides.  The proposal for each RspT shall identify:

(a)		Controlling Entity;

(b)		Following Entity;

(c)		Congestion Zone;

(d)		Maximum value;

(e)		Units supplying energy; and

(f)		Other information required by ERCOT.

Reference:  Protocol Section 4.9.4.2, Principles for Responsibility Transfers

(1)	RspT may be used to shift responsibility for Supply of a defined maximum amount of MWs from one QSE to another QSE within the same Congestion Zone after the close of the Adjustment Period.  As the RspT changes the responsibility for Supply of one QSE there must be an equal and opposite change in the responsibility for Supply of the other QSE.

(2)	One of the QSEs will act as the controller of the Real Time Dynamic signal.  That Controlling Entity (CE) will send a Real Time power signal to ERCOT representing that QSE’s power commitment to the other QSE, the Following Entity (FE).

(3)	ERCOT will use the dynamic power signal from the CE in its calculation of the CE’s SCE.  ERCOT will also use the dynamic power signal from the CE to calculate an equal and opposite value to use in calculation of the FE’s SCE.  The FE will use a signal from the CE to calculate its (the FE’s) SCE.

(4)	ERCOT will integrate the dynamic power signal from the CE for each Settlement Interval and use this value as an offset in the CE’s settlement for Resource imbalance.  An equal but opposite offset will be used in the FE’s settlement for Resource imbalance.

(5)	If the signal from the CE is lost, ERCOT will use the last good value received from the CE until the CE manually replaces the value, or the signal is restored.

[PRR428: Add Section 4.9.4.3 upon system implementation] 4.9.4.3 Principles for Responsibility Transfers For RMR Units (1) RspT may be used to schedule energy from an RMR Resource’s QSE to ERCOT. (2) The RMR Resource’s QSE will act as the controller of the Real Time Dynamic signal. The QSE will send a Real Time power signal to ERCOT representing the amount of RMR energy being delivered from RMR Resources to ERCOT by Congestion Zone. The dynamic signal will be consistent with and will not exceed the RMR deployment instructions from the final Delivery Plan and/or subsequent Adjustment Period changes, and the operation and availability of the RMR Resources. (3) ERCOT will use the dynamic power signal from the RMR QSE in its calculation of the RMR QSE’s SCE. (4) ERCOT will integrate the dynamic power signal from the RMR QSE for each Settlement Interval and use this value as an offset in the RMR QSE’s settlement for Resource imbalance. (5) If the signal from the Controlling Entity (CE) is lost, ERCOT will use the last good value received from the CE until the CE manually replaces the value, or the signal is restored.

Reference:  Protocol Section 4.9.5, Responsibility Transfer for Balancing Energy Bidding

Certain PUCT mandated Capacity Auction Products (as defined in PUCT S.R. §25.381) allow the entitlement holder (Buyer) to provide Balancing Energy Service to ERCOT whenever a Responsibility Transfer (“RspT”) between Buyer and Seller’s respective QSEs is established.  The procedure for providing Balancing Energy from Capacity Auction Products is set forth in Protocols Section 6.5.2.1, Balancing Energy Service Bids from Bilateral Contracts.

## 3.3	Document Control

Authorities

| Prepared by | Date Completed | Reviewed by | Date Authorized |
| --- | --- | --- | --- |
| B. Garza | April 17, 2001 | ROS |  |
| I. Flores | April 15, 2002 | OGRTF/ROS |  |
| I. Flores | 30 September 2002 | OGRTF/ROS |  |
| I. Flores | 1 December 2002 | OGRTF/ROS |  |
| I. Flores | 1 January 2003 | OGRTF/ROS |  |
| I. Flores | 1 April 2003 | OGRTF/ROS |  |
| J. Gilbertson | 29 August 2003 |  |  |

Distribution List

| Name | Organization |
| --- | --- |
| Reliability Operations Subcommittee | Technical Advisory Committee |

Change History

| Issue/Date | Reason for issue |
| --- | --- |
| Version 1.0 February 28, 2001 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee |
| Version 1.0a March 2, 2001 | Inserted sections 3.2.4.2 – 3.2.4.4 |
| Version 1.1 April 16, 2001 | Clarified sections 3.2.4.2 – 3.2.4.4 |
| May 1, 2002 | OGRR101 |
| October 1, 2002 | OGRR113 |
| December 1, 2002 | OGRRs 114 & 116. Revised Sections 3.1.4.2, 3.1.4.3, 3.1.3.2 & 3.2.2.1 to match the Protocols references. |
| January 1, 2003 | OGRR119, revised Section 3.1.3.1 to add a backup plan requirement for QSEs. |
| April 1, 2003 | OGRR125 – updated Protocols referenced in Sections 3.1.3.2, 3.2.1.2, 3.2.2.1 & 3.2.6. OGRR126 – updated reference in Section 3.2.6 citing Protocols Sections 4.9.1. 4.9.2 & 4.9.3 and deleted redundant text after reference. |
| September 1, 2003 | OGRR130 – revised Section 3.1.4.1 & 3.1.4.5. OGRR134 – revised Section 3.1.6. |
| April 1, 2004 | OGRR142 – revised Section 3.1.3.4 & 3.1.5.1. |
| May 1, 2004 | OGRR144 – revised Section 3.1.4.6 OGRR146 – revised Section 3.1.3.4 & 3.1.4.8. |
| June 1, 2004 | OGRR145 |
| November 1, 2004 | OGRR152 and fixed typographical errors in Protocol references |
| December 1, 2004 | OGRR153; Admin OGRR160 |
| June 1, 2005 | Admin OGRR168 |
| November 1, 2005 | OGRR154 |
| February 1, 2006 | Admin OGRR180 |
| June 1, 2006 | OGRR169, OGRR176, Admin OGRR185 |
| February 1, 2007 | Admin OGRR190 |
| March 1, 2007 | Admin OGRR191 |
| July 1, 2007 | Admin OGRR201 |
| May 1, 2008 | Admin OGRR207 |

Note that it is allowed by these guides and Protocols for the QSE to submit the maximum generation within a 168 hour period and submit without any special testing effort.  A form is provided within these guides for submission of test results.