Question #5: Compliance / Performance Measures -- 24/7 communication must be available for TSP to reach wind generators 
The following requirements for generation operators are proposed in order to continuously support the reliable operation of the ERCOT system:
1) Adjust voltage set point 	5 minutes to change injection point voltage value using necessary means (e.g. capacitor or reactor switching, LTC tap, generator setpoint) in normal operating conditions
2) Adjust reactive output 	Same as No. 1.
3) Adjust MW output 		Response times as defined in the applicable ERCOT Protocols
4) Switch breaker or switch 	15 minutes for devices that interconnect the facility to the transmission system
5) Tap LTC 			whatever is necessary to maintain compliance with item 1.
6) Start unit 			10 minutes to begin start sequence
7) Shut down unit 		5 minutes to begin shutdown sequence
8) Blackstart Instructions 	5 minutes for available units
A phone number with 24 hour response is available to ERCOT and the TSP registered for the facility at which the TSP and ERCOT can always get response as listed above.