| OGRR Number | 209 | OGRR Title | Administrative Changes for June 1, 2008 Operating Guides |
| --- | --- | --- | --- |
| Date Posted | May 7, 2008 |
| Status | Administrative Change |

| Operating Guide Section Requiring Revision | 4.5.3.3, EECP Steps |
| --- | --- |
| Protocol Section(s) Requiring Revision, if any | None. |
| Revision Description | This Administrative Operating Guide Revision Request (OGRR) updates the ERCOT Load Shed Table for 2008. |
| Reason for Revision | Administrative change to update the ERCOT Load Shed Table as allowed by Section 1.3, Process for Operating Guide Revision. |

| Sponsor |
| --- |
| Name | Leo Villanueva on behalf of ERCOT |
| E-mail Address | evillanueva@ercot.com |
| Company | ERCOT |
| Company Address | 2705 West Lake Drive Taylor, TX 76574 |
| Phone Number | 512-248-3135 |

| Market Rules Staff Contact |
| --- |
| Name | Giriraj Sharma |
| E-Mail Address | gsharma@ercot.com |
| Phone Number | 512-248-6759 |

Proposed Operating Guide Language Revision

#### 4.5.3.3	EECP Steps

Step 1 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal To 2300 Mw

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | Utilize available DC tie capability that is not already being used by the market. Notify the Southwest Power Pool Security Coordinator. Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency. Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers. |
| QSE | Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency. |

Step 2 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal To 1750 MW

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures associated with STEP 1 |
| ERCOT | Instruct TDSPs to reduce Customer Loads by using distribution voltage reduction measures, if deemed beneficial by the TDSP. Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (LaaRs) (controlled by high-set under-frequency relays) With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer Load from the ERCOT control area to Non-ERCOT control areas. Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation. Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation. |

Step 3 - Maintain System Frequency At 60 Hz

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 and 2. |
| ERCOT | Deploy all available EILS Resources as a single block via a single Verbal Dispatch Instruction to all QSEs providing EILS. |

Step 4 - Maintain System Frequency At 59.8 Hz Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1, 2, and 3. |
| ERCOT | Direct all TDSPs and their agents to shed firm Load, in one hundred (100) megawatt (MW) blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hertz (Hz). ERCOT may take this action prior to the expiration of the ten (10) minute EILS Resource deployment period if ERCOT, in its sole discretion, believes that shedding firm Load is necessary to maintain the stability of the ERCOT System. If, due to ERCOT System conditions, EILS Resources are not deployed prior to this action, ERCOT shall deploy EILS Resources as soon as possible following this action. |
|  | In addition to measures under STEPS 1 and 2. |
| TDSPs | Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop Load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan. |

Obligation for Load shed is by DSP.  Load shedding obligations need to be represented by an Entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of Entities.]

ERCOT Load Shed Table

| Transmission Operator | 2007 Total Transmission Operator Load (MW) |
| --- | --- |
| American Electric Power | 8.85 |
| Austin Energy | 3.83 |
| Brazos Electric Power Cooperative | 4.26 |
| CenterPoint Energy | 26.67 |
| City of Bryan | .53 |
| City of College Station | .28 |
| City of Denton | 0.49 |
| City of Garland | 0.95 |
| CPS Energy | 6.92 |
| Lower Colorado River Authority | 4.95 |
| Magic Valley Electric Cooperative | 0.58 |
| Oncor | 37.20 |
| Public Utility Board of Brownsville | 0.42 |
| Rayburn Country Electric Cooperative | 0.98 |
| South Texas Electric Coop-Medina Electric Coop | 0.59 |
| Texas New Mexico Power | 2.38 |
| Tex-La | 0.13 |
| ERCOT Total | 100.00 |