ERCOT Operations Report

April 2008 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 4/1/2008 12:59 | 59.876 | 00:12 | Unit trip with 530 MW online |
| 4/1/2008 18:03 | 60.101 | 01:16 | SCE change +300 MW and steel mill load drop 200 MW. |
| 4/2/2008 21:45 | 59.854 | 00:42 | Unit trip with 650 MW online |
| 4/3/2008 9:25 | 59.805 | 00:44 | Unit trip with 740 MW online |
| 4/4/2008 9:16 | 59.894 | 00:02 | Unit trip with 200 MW online |
| 4/4/2008 14:41 | 59.853 | 00:02 | Unit trip with 640 MW online |
| 4/4/2008 22:22 | 59.837 | 00:14 | Unit trip with 644 MW online |
| 4/5/2008 0:03 | 59.899 | 00:02 | SCE change -500 MW (in approximately 10 min) |
| 4/9/2008 21:54 | 60.104 | 00:04 | SCE change +300 MW and steel mill load drop 200 MW. |
| 4/9/2008 22:06 | 60.101 | 08:05 | Out of DRS. SCE change +500 MW. |
| 4/10/2008 1:02 | 60.101 | 07:29 | Out of DRS. Overshot balance up instruction to recover URS. |
| 4/10/2008 3:47 | 59.86 | 01:08 | Unit trip with 720 MW online |
| 4/12/2008 14:18 | 59.898 | 00:04 | Unit trip with 650 MW online |
| 4/13/2008 4:06 | 60.102 | 00:12 | SCE change +1000 MW (10 min). |
| 4/17/2008 13:27 | 59.865 | 00:29 | Unit trip with 552 MW online |
| 4/18/2008 0:03 | 60.106 | 02:57 | SCE change +800 MW. |
| 4/19/2008 6:00 | 60.101 | 01:00 | SCE change + 700 MW. |
| 4/23/2008 13:08 | 59.833 | 00:20 | Unit trip with 587 MW online |
| 4/24/2008 23:26 | 59.898 | 00:08 | Unit trip with 561 MW online |
| 4/25/2008 3:37 | 59.898 | 00:04 | Unit trip with 200 MW online |
| 4/25/2008 22:04 | 59.893 | 00:04 | Multiple Unit trips with 535 MW online. |
| 4/27/2008 1:03 | 60.106 | 00:04 | SCE change +350 MW and steel mill load drop 200 MW. |
| 4/29/2008 21:06 | 60.104 | 00:56 | SCE change +450 MW and steel mill load drop 100 MW. |

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 4/1 12:59:25 | 4/1 13:19:10 | 0:19:45 | 541.63 |  |
| 4/1 20:09:38 | 4/1 20:17:36 | 0:07:58 | 322.9 | Out of URS. System Load Pickup |
| 4/2 21:45:32 | 4/2 22:16:54 | 0:31:22 | 630.18 |  |
| 4/3 9:25:02 | 4/3 9:46:31 | 0:21:29 | 859.32 |  |
| 4/4 1:33:22 | 4/4 1:50:34 | 0:17:12 | 328.10 | Input error in offset calculation. |
| 4/4 9:16:08 | 4/4 9:28:32 | 0:12:24 | 395.81 |  |
| 4/4 14:41:42 | 4/4 14:57:30 | 0:15:48 | 609.34 |  |
| 4/4 22:22:50 | 4/4 22:54:58 | 0:32:08 | 692.66 |  |
| 4/5 0:03:38 | 4/5 0:15:26 | 0:11:48 | 369.78 |  |
| 4/8 12:53:00 | 4/8 13:02:00 | 0:09:00 | 359.35 | Unit trip |
| 4/9 23:57:52 | 4/10 0:36:42 | 0:38:50 | 343.74 | Out of URS. SCE |
| 4/10 3:47:22 | 4/10 4:12:09 | 0:24:47 | 713.5 |  |
| 4/11 23:32:32 | 4/11 23:40:40 | 0:08:08 | 322.9 | Instantaneous ramp to constraint instruction. |
| 4/12 14:18:52 | 4/12 14:49:24 | 0:30:32 | 374.99 |  |
| 4/13 4:19:14 | 4/13 4:42:20 | 0:23:06 | 359.35 | SCE |
| 4/16 22:05:47 | 4/16 22:16:11 | 0:10:24 | 328.1 | SCE |
| 4/17 13:27:01 | 4/17 13:46:21 | 0:19:20 | 723.91 | Unit trip |
| 4/19 1:32:03 | 4/19 1:44:17 | 0:12:14 | 354.15 | SCE |
| 4/19 16:14:25 | 4/19 16:25:43 | 0:11:18 | 317.69 | SCE & Steel Mill Pickup |
| 4/21 23:32:58 | 4/21 23:46:26 | 0:13:28 | 322.9 | SCE |
| 4/22 6:11:28 | 4/22 6:17:34 | 0:06:06 | 317.69 | SCE |
| 4/23 13:08:42 | 4/23 13:30:01 | 0:21:19 | 713.5 |  |
| 4/23 16:19:00 | 4/23 16:59:50 | 0:40:50 | 333.33 | Out of URS. SCE |
| 4/23 22:04:08 | 4/23 22:15:30 | 0:11:22 | 348.94 | SCE |
| 4/24 20:31:02 | 4/24 20:45:14 | 0:14:12 | 322.9 | Overshot balance down instruction to recover down reg |
| 4/24 23:26:18 | 4/24 23:47:02 | 0:20:44 | 479.15 |  |
| 4/25 1:07:30 | 4/25 1:18:52 | 0:11:22 | 328.1 | Out of URS |
| 4/25 3:37:08 | 4/25 3:58:40 | 0:21:32 | 374.99 |  |
| 4/25 16:22:17 | 4/25 16:39:20 | 0:17:03 | 343.74 | Unit trip |
| 4/25 22:04:34 | 4/25 22:20:28 | 0:15:54 | 401.01 |  |
| 4/28 12:18:42 | 4/28 12:32:52 | 0:14:10 | 333.33 | Unit trip |
| 4/30 9:52:08 | 4/30 10:06:36 | 0:14:28 | 333.33 | Out of URS. Telemetry issues causing input error in offset calculation. |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 0 | 0 | 7 | 7 |
| Bryan Area | 0 | 13 | 0 | 0 | 13 |
| Corpus | 0 | 0 | 0 | 1 | 1 |
| DFW | 0 | 102 | 0 | 1 | 103 |
| E RIO | 0 | 8 | 26 | 0 | 34 |
| Houston | 0 | 25 | 3 | 3 | 31 |
| Laredo | 59 | 0 | 0 | 0 | 59 |
| North | 0 | 3 | 1 | 0 | 4 |
| Northeast | 0 | 0 | 0 | 4 | 4 |
| San Antonio | 0 | 0 | 0 | 1 | 1 |
| South | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 6 | 12 | 0 | 18 |
| Western | 0 | 4 | 10 | 3 | 17 |
|  | 59 | 161 | 52 | 20 | 292 |

| Historical Totals | Apr-07 | Mar-08 | Apr-08 |
| --- | --- | --- | --- |
| Austin | 76 | 10 | 7 |
| Bryan Area | 9 | 7 | 13 |
| Corpus | 2 | 2 | 1 |
| DFW | 18 | 6 | 103 |
| E RIO | 1 | 19 | 34 |
| Houston | 6 | 7 | 31 |
| Laredo | 55 | 59 | 59 |
| North | 0 | 4 | 4 |
| Northeast | 0 | 10 | 4 |
| San Antonio | 20 | 2 | 1 |
| South | 1 | 0 | 0 |
| W RIO | 5 | 0 | 18 |
| Western | 7 | 60 | 17 |
| Total | 200 | 186 | 292 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Matador – Paducah Clare Street 69kV | Girard Tap – DKEC Jayton 69kV | 6 |
| Morgan Creek SES – Quail SW & Odessa EHV 345kv | Big Springs SW – Big Spring West 138kV | 6 |
| North Edinburg – Rio Hondo 345kV | South McAllen – Stewart Road 138kV | 6 |
| Morgan Creek SES – Cal Energy 345kV | Big Springs SW – Big Spring West 138kV | 4 |
| Calaveras – Skyline & Walzem Road 138kV | Calaveras – Ballpark 138kV | 3 |
| Calaveras – Skyline & Walzem Road 138kV | Five Points – Westside 138kV | 2 |
| Jewett – TH Wharton & Tomball 345kV | Peter Reit Auto | 2 |
| Martin Lake SES – Stryker Creek SES & Mt Enterprise SW 345kV | Delek POI – Tyler East 138kV | 2 |
| Martin Lake SES – Stryker Creek SES & Mt Enterprise SW 345kV | Delek POI – Tyler Northeast 138kV | 2 |
| Moss Switch – Holt Switch 138kV | Odessa North 138/69kV Auto | 2 |
| Mt. Enterprise SW – Trinidad SES & Martin Lake SES – Stryker Creek 345kV | Nacogdoches SE Auto 345/138kV | 2 |
| South Channel – Jefferson 138kV | Jefferson – Crown 138kV | 2 |
| Benbrook SW – Parker SW – Graham SES 345kV | Flat Creek – Leon Switch 138kV | 1 |
| Big Brown SES – Jewett 345kV | Richland Chambers – Trinidad SES 345kV | 1 |
| Duke – Pharr MVEC 138kV | Hall Acres – South McAllen 138kV | 1 |
| Jewett – TH Wharton & Tomball 345kV | Garott – Midtown | 1 |
| Jewett – TH Wharton & Tomball 345kV | Robertson – Watson Chapel 138kV | 1 |
| Jewett – TH Wharton & Tomball 345kV | Goldthwaite 138/69kV Auto #2 | 1 |
| King Reit – Kuykendahl – Roans Prairie Reit & Jewett – Tomball 345kV | Midtown – Garrott 138kV | 1 |
| LaPalma – Loma Alta 138kV | Union Carbide – Loma Alta 138kV | 1 |
| Zorn – Lytton Springs & Austrop 345kV | Canyon – Rohr 138kV | 1 |
| Martin Lake SES – Stryker Creek SES & Mt Enterprise SW 345kV | Nacogdoches SE Auto 345/138kV | 1 |
| Martin Lake SES – Stryker Creek SES & Mt Enterprise SW 345kV | Tyler Northeast – Shamburger 138kV | 1 |
| Matador – Spur 69kV | Matador – Paducah Clare Street 69kV | 1 |
| Midland East – Odessa EHV SW 345kV | Odessa Southwest – Moss Switch 138kV | 1 |
| Morgan Creek SES – Cal Energy 345kV | Stanton East SW – Midland East 138kV | 1 |
| Moss Switch – Holt Switch 138kV | Odessa North – North Cowden 69kV | 1 |
| North Edinburg 345/138kV Auto #1 | North Edinburg 345/138kV Auto #2 | 1 |
| Oasis – PH Robinson 345kV | Garott – Midtown | 1 |
| Pawnee – Sam Rayburn Switchyard 138kV | Sam Rayburn Switchyard 138/69kV Auto #2 | 1 |
| Royse SW – Farmersville 345kV | Collin SES – Frisco 138kV | 1 |
| San Miguel Switchyard – Dilley Switch 138kV | Derby Sub – Pearsall SW 69kV | 1 |
| Uvalde CSW – Hamilton 138kV | Hamilton – Maverick 138kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 26 |
| North-South | 16 |
| North-Houston | 15 |
| South-North | 11 |
| North –West | 4 |

New RAP

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 04/02/2008 | Frequency Control Desk procedure V3R64 | 368 |
| 04/02/2008 | Transmission and Security Desk V3R90 | 367 |
| 04/02/2008 | Shift Supervisor Desk Procedure V3R46 | 366 |

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

4/13 	Held the 08:45 deployments, resumed at 09:30 due to a database problem with the MOI causing it to fail to execute.

4/15  	Held 08:30 balancing deployments, resumed at 09:00 due to 08:45 deployments failed to execute due to market database issues.

4/18  	Held IE 18:15 balancing deployments, resumed at 18:45 due to IE 18:30 deployments failed to execute due to market database interconnect configuration.

4/21  	Alert issued due to holding IE 08:45 balancing deployments, resumed at 09:30 due to IE 09:00 and 09:15 failed to execute.   This was due to a storage array failure.

4/21  	Alert issued due to holding IE 11:00 balancing deployments due to IE 11:15, 11:30, 11:45, 12:00 and 12:15 failed to execute.  Resumed with IE 12:30 deployments. This was due to a storage array failure.

Communication

None

## ERCOT peak (Unofficial)

04/22 	   18:00   46,085 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | 3.59 |
| March | 3.41 | 4.95 | 2.70 | 3.29 |
| April | 3.37 | 5.59 | 3.00 | 2.45 |
| May | 4.21 | 3.59 | 3.22 | NA |
| June | 3.91 | 2.65 | 4.46 | NA |
| July | 5.22 | 2.62 | 4.29 | NA |
| August | 4.86 | 2.09 | 3.11 | NA |
| September | 6.24 | 4.03 | 3.78 | NA |
| October | 4.51 | 3.63 | 3.08 | NA |
| November | 4.53 | 3.28 | 2.95 | NA |
| December | 5.95 | 3.44 | 3.74 | NA |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.16 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 4/14/08 | 1:50 | 3:30 | OCN issued due to capacity insufficiencies HE 0700 - 0900. |
| 4/14/08 | 3:30 | 6:00 | Alert issued due to capacity insufficiencies HE 0700 - 0900. |
| 4/21/08 | 22:00 | 23:59 | OCN issued for capacity shortage for hours 15:00 to 23:00 on 4/22/08. |
| 4/22/08 | 0:00 | 0:45 | ERCOT opened an Adjustment Period Replacement Reserve Market for hours 15:00 - 23:00 due to capacity shortage. |
| 4/22/08 | 14:24 | 21:15 | Advisory ARR below 3000 MW. |
| 4/22/08 | 16:15 | 21:15 | Deployed Non Spin Reserve Service due to depleting Up Balancing bid stack |
| 4/24/08 | 3:30 | 11:00 | Issued OCN for capacity shortage for hours 15:00 - 20:00. |

Transmission

None

Other

4/12 	Held the 23:00 interval, resumed with interval ending 23:30 due to input error in offset calculation.

4/24  	Held the real-time balancing deployments for IE 16:45 and resumed with IE 17:15 deployments.

Texas RE Event Analysis

4/03     01:10	Simultaneous loss of Oklaunion – Bowman Switch, Oklaunion – Abilene Mulberry Creek 345 kV lines and one 345/138 kV Autotransformer at Oklaunion.

4/09     17:25	Simultaneous loss of Graham SES – Breckenridge, Breckenridge – Tap,  Graham SES – Leon Switch 138 kV lines, and one 138/69 kV Autotransformer at Breckenridge.

4/10	03:47	DCS Event

Simultaneous loss of one unit and the East DC Tie totaling 1083 MW, and Venus #2 Bus tripped which has lines going to Liggett, Everman, Tradinghouse, Big Brown , Webb, Midlothian ANP and 345/138 kV #2 Autotransformer to Chaparral.

SPS Operations

There were 13 SPS Operations in the first three months of 2008.

In January there were seven, three misoperations were due to incorrect relay settings, one misoperation due to failure for unit to ramp back, and three operated as intended.

In February there were two and both were determined to be misoperations due to failure for unit to ramp back.

In March there were four and all were determined to be misoperations due to failure for unit to ramp back.