## Slide 1: Black Start
Twenty-Fourth Annual ERCOT Operations Training Seminar

## Slide 2: Objectives
Identify the duties and responsibilities of ERCOT when performing the Black Start Plan.
List the data/information non-disclosure requirements for Transmission System Operators during Black Start activities.

## Slide 3: Black Start
Black Start Service
  A contracted Ancillary Service acquired by ERCOT for the benefit of all Loads, provided by Resource capable of starting without support of the ERCOT Transmission Grid.
Black Start Resource
  A single Resource capable of providing Black Start Service.

## Slide 4: Black Start Services
Black Start services are needed in the event of partial or complete collapse of electric system.
These services are provided by a set of contracted Black Start capable generation units
These units are re-evaluated annually.

## Slide 5: Black Start Units
To qualify for Black Start service, a resource must:
  Be capable of self-starting without support from ERCOT system or
  Be within close proximity of another power pool which are capable of starting from such power pool via a firm standby power supply contract, and

## Slide 6: Black Start Units
  Be selected by ERCOT based on selection criteria, and
  Pass four resource tests

## Slide 7: Black Start Unit Selection
Every year, interested black start capable Resource entities may submit their responses to the Request For Proposal (RFP) by ERCOT, to provide Black Start services for the next calendar year.
ERCOT uses the following selection criteria to select a set of units with minimum cost:
  Simulated restoration of 90% expected peak load within a pre-determine number of hours.
  Expected restoration off-site power to nuclear units within 8 hours.
  Proximity of Black Start units to major load centers.

## Slide 8: Black Start Unit Selection Criteria
There are two different types of selections:
  Group Selection
    Bid price ($/hour)
    Amount of MW pickup (MW)
    Restoration time (hours)
  Specific resource selection
    Black Start MW, next-start MW capacity, start-up time
    Proximity to nuclear plant
    Proximity to load centers

## Slide 9: Black Start Unit Selection Methodology
A Microsoft Access program was written to determine the best set of units which will fulfill all the selection criteria in an automated fashion.
The program simulates the total unit start up time, ramp-up time, crew travel time, and next-start ramp-up time to meet selection criteria. Every Black Start Unit will continuously be starting next start units and through it other units down the line, without waiting for other Black Start Units to start up.

## Slide 10: Black Start Unit Testing
Every Unit that gets selected through the above selection criteria needs to undergo the following four tests.
  Basic Start-up Test (Every Year)
  Line Energizing Test (Every 3 years)
  Load Carrying Test (Every 6 years)
  Start up Next Start resource’s largest required motor (Once as long as the same Next Start resource is available) (Can be simulation or physical test)

## Slide 11: Black Start Timeline
April 1st : ERCOT will publish the RFP
June 1st: Last Day for Black Start resources to submit their responses to RFP
August 1st: ERCOT will publish the list of pre-selected units to provide Black Start Services
August 1st – September 1st : ERCOT will train it’s employees to be witnesses to Black Start Testing

## Slide 12: Black Start Timeline
September 1st to November 1st : Pre-selected Black Start units should schedule their testing.
November 1st – December 1st : Time to schedule re-tests if any. All testing must be completed by end of November.
November 15th : TOs submit their respective TO Black Start Plans to ERCOT.
January 1st: ERCOT will post the ERCOT Black Start Plan and the ERCOT Black Start Map for the following year.

## Slide 13: ERCOT Black Start Plan
In the event of a major system disturbance it is necessary to have procedures in place to cope with events and restore the system to normal state as quickly as possible.
ERCOT Black Start Plan incorporates restoration effort in case of partial or complete collapse of electric system.

## Slide 14: ERCOT Black Start Plan
What is in a Black Start Plan?
  Black Start map and transmission corridors
  Principles
  Strategies
  Priorities
  Responsibilities
    ERCOT
    TOs
    QSEs
    Resources

## Slide 15: Black Start Plan - Principles
Contracted Black Start Units
Local TO Plans
  Primary/Secondary Transmission Corridors
  Designated synchronization points, primary and alternatives
Mutual assistance and cooperation
Restore the power system

## Slide 16: Black Start Plan - Principles
Example of a Transmission Corridor

## Slide 17
INTENTIONALLY BLANK

## Slide 18: Black Start Plan - Principles
Each contracted Black Start Resource and TO will have an internal Black Start plan.
Plans should identify Black Start Units, primary and secondary Next Start units, stabilizing loads, primary and secondary transmission corridors and synch points between islands.
The power system, not customers, is the principal focus during the restoration effort.

## Slide 19: Black Start Plan -Strategies
In the event of a total ERCOT blackout, the market is suspended. Any data/information transfer required to support power system restoration shall be provided.
All information shared with affiliates for the restoration process is an allowed corporate support service under the provisions of PUCT rule 25.272. (Suspension of confidentiality requirements)
35 contracted Black Start resources.
18 Black Start sites.

## Slide 20: Black Start Plan -Strategies
The initial 15 islands will be built and maintained solely under the direction of the TOs as outlined in the TO Black Start Plans.
The TOs will be responsible for maintaining appropriate voltage levels and reactive controls during the restoration.

## Slide 21: Black Start Plan -Strategies
The TOs should periodically update ERCOT on the status of the islands during the restoration process. These updates should coincide with the following events:
  A Black Start unit is successfully brought on line.
  Any additional generation that is brought on line.
  A designated synchronization point between islands is reached.
  The TO needs to energize a piece of equipment that belongs to another TO.
  Any time a collapse or regression occurs in the restoration process.

## Slide 22: Black Start Plan - Priorities
Generating Plants will secure and/or stabilize units where necessary.
Transmission corridors will be prepared as necessary to support restoration.
Assess ERCOT system condition, and available communication facilities.
Restore and maintain communication facilities to the extent possible.
Contracted Black Start units will immediately begin preparations to bring their units on line in coordination with their TO.
Designated TOs will begin building islands with the goal of reaching designated synchronization points.

## Slide 23: Black Start Plan - Priorities
As islands are being built the following loads should take priority.
  Nuclear generating facilities.
  Critical power to as many generating units as possible to prevent equipment damage.
  Startup power for generating units that do not have Black Start capability.
  ERCOT
  Military facilities
  Law enforcement organizations and facilities affecting public health.

## Slide 24: Responsibilities - ERCOT
Maintain continuous surveillance of the status of the ERCOT system.
Act as a central information collection and dissemination point for the region.
Coordinate reconnection of transmission.
Direct assistance for QSEs, TOs, PGCs, and Market Participants.
Direct the distribution of reserve.
Coordinate the return of the ERCOT system to Automatic Generation Control.

## Slide 25: Responsibilities -TO
Shall communicate with local Black Start Units and coordinate switching to next start units and local load.
Shall implement its local Black Start Plan.
Shall follow the direction of ERCOT on behalf of represented TDSPs.
Shall act as the regional ERCOT representative in coordinating interconnection of units.
Shall follow the direction of ERCOT for reconnection of islands.

## Slide 26: Responsibilities – QSE and PGC
Take immediate steps to initiate the local Black Start Plan.
Supply ERCOT and/or the local TO with information on the status of generation, transmission, and communication facilities.
Follow the direction of the local TO or ERCOT in picking up local load and starting next units.
Provide available assistance as directed by ERCOT or the local TO.

## Slide 27: Summary
Please remember the success of a plan like this relies heavily on accurate communication and well trained operators.
Thank you for your time and attention.
Questions?