## Slide 1
Load Shed Requirements
Notes: 17 April 2006<number>

## Slide 2
Introduction
System threatening events can happen so quickly that there is little time for preventative measures or they can progress slowly allowing time for operator intervention. The shedding of firm system load is the last line of defense in preventing complete grid failure due to frequency decay, cascading outages or collapsing voltages. Reduction of system load can be accomplished automatically through relay action or manually as a result of operator intervention. System operators are authorized to shed system load in order to save the grid from collapse without seeking approval from anyone. System operators must know when and how to administer this infrequently used tool.
Notes: Most system operators are taught that dropping customer load is the worst mistake they could make. If they make a switching error resulting in loss of load they can be terminated. If they observe customer outages they should expend every effort to restore service as quickly as possible. Their whole world is centered around keeping the lights on. There is no wonder that an operator could be hesitant to drop load when necessary to save the system. Operators need to be confident that when the system is on the brink of failure, load shed is the right tool for the job. These operators need to be able to forsee and recognize conditions leading to a collapse and act quickly and effectively to guard against grid failure. Much like a policemans gun, this is the one tool system operators need to be intimately familiar with, but you hope they never have to use it.

## Slide 3
Objectives
At the completion of this course of instruction you will be able to:
explain the differences between automatic and manual load shed procedures and implementation
list the frequency triggers for automatic load shed
explain the load replacement procedure
describe where to locate the ERCOT Load Shed Table
explain an operators authority to implement load shed procedures

## Slide 4
Load Shed Purpose
Arrest Frequency Decay
Restore Reserves
Prevent Voltage Collapse
Relieve Overloads

## Slide 5: Arrest Frequency Decay
Hertz
60
59
61
Notes: Frequency is affected by the balance between load and generation. As you can see, any change to either upsets the balance. In circumstances where generation cannot be increased, reducing load is the only way to restore frequency.

## Slide 6: Restore Reserves
Load in MW
Notes: When generators are loaded to capacity, shedding load can give a system more regulating room.

## Slide 7: Prevent Voltage Collapse
125.4
134.2
138.0
Notes: While the frequency is essentially the same across the grid, voltages can vary greatly from buss to buss dependant on several factors. Some TO’s in ERCOT have installed relays that can detect low voltage points and shed load if the voltage remains critically low for a predetermined time. Load would be shed on those busses to prevent a local voltage collapse.

## Slide 8: Relieve Overloads
150
120
10
10
10
140
130
120

## Slide 9: Automatic vs. Manual
Automatic load shed is initiated by relay action in response to system frequency or voltage events
  Blocks 1, 2 & 3
Manual load shed is initiated by operator action in cases where threats are foreseen with enough time to take action
  Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.
  Block 4

## Slide 10: EECP Step 3
“ERCOT has implemented EECP Step 3. ERCOT is instructing all Transmission Operators to shed their share of <amount> MWs. Transmission Operators are to report to ERCOT when this task is complete and give the amount of load shed.”
ERCOT Operating Procedure Manual, Transmission & Security Desk, 2.5.6
Notes: Warn about hanging up on a Hot Line call. Hang-ups are disruptive. Stay on the line until the call is over.

## Slide 11
Transmission Operator | 2005 Total Transmission Operator Load (MW)
American Electric Power | 9.50
Austin Energy | 3.90
Brazos Electric Power Cooperative | 3.89
CenterPoint Energy | 24.56
City of Bryan | 0.53
City of College Station | 0.29
City of Denton | 0.50
City of Garland | 0.99
City Public Service of San Antonio | 7.05
Lower Colorado River Authority | 4.96
Magic Valley Electric Cooperative | 0.53
Public Utility Board of Brownsville | 0.41
Rayburn Country Electric Cooperative | 1.00
South Texas Electric Coop-Medina Electric Coop | 0.60
Texas New Mexico Power | 2.26
Tex-La | 0.15
TXU-Electric Delivery | 38.88
ERCOT Total | 100.00
ERCOT Guides 4.5.3.3
Notes: Percentages for Step 3 Load shedding will be based on the previous year's TDSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

## Slide 12: Triggers
Automatic Load Shed (relay initiated)
    59.3 – 5%
    58.9 – 10% (additional)
    58.5 – 10% (additional)
Manual Load Shed (operator initiated)
    Total shed amount determined by ERCOT operators
    Each TO responsible for a share of the total
    Shares updated annually
      ERCOT Guides, Section 4
    Hotline call initiated

## Slide 13: Triggers
Voltage
  .91 PU for 3 sec. (Block 1)
  .91 PU for 5 sec. (Block 2)
  .91 PU for 8 sec. (Block 3)
Localized protection as well as global

## Slide 14: Automatic Load Shed Time Delay
TDSPs shall ensure that the under-frequency relays connected to each load will operate with a fixed time delay of no more than 30 cycles. Total time from the time when frequency first reaches one of the values specified above to the time load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.
ERCOT Guides 2.9.1
Notes: 30 cycles equals a half a second.

## Slide 15: Load vs. Resource
Frequency Threshold | Load Relief
59.3 Hz | 5% of the ERCOT System Load (Total 5%)
58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%)
58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%)
Frequency Range | Delay to Trip
Above 59.4 Hz | No automatic tripping (Continuous operation)
Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes
Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds
Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds
57.5 Hz or below | No time delay required
Generating Unit Underfrequency Relaying
Distribution Ckt. Underfrequency Relaying
ERCOT Guides 2.9.1
ERCOT Guides 2.9.2
Notes: Underfrequency relays at substations are coordinated with underfrequency relays at generating units. Sustained off frequency operation of generators can result in damage and force an extended and very expensive outage.

## Slide 16: Automatic Load Shed Considerations
If a loss of load occurs due to the operation of under-frequency relays, a TO may rotate the physical load interrupted to minimize the duration of interruption experienced by individual customers or to restore the availability of under-frequency load-shedding capability; however, in no event shall the initial total amount of load without service be decreased by a TO without the approval and direction of the ERCOT System Operator.
ERCOT Guides 2.9.1

## Slide 17: Rolling Outages
Limit the amount of time customers power is off
Spreads the outages over a wider area
Rotation period determined by TO/DSP
  15 min.
Must maintain minimum requested MW shed amount

## Slide 18: Load Replacement
Restoring Automatic Protection following an event
  Trip Block 4 loads equal to the amount of load shed by automatic relaying (small increments)
  Restore Block 1, 2 & 3 loads to regain automatic relay protection
  Under the direction of ERCOT operators
Not to be confused with an automatic load restoration scheme
Notes: When frequency has fallen enough to initiate automatic under-frequency load shed, the system has been stripped of under-frequency relay protection. Should another event occur under these conditions there would not be any automatic protection to protect the system. Replacing the tripped Block 1, 2 & 3 loads with Block 4 loads will restore automatic protection without jeopardizing the system. This should only be done under the direction of ERCOT operators since the system may be unstable.

## Slide 19: Mechanics
UFC
Relay
RTU
System Frequency
SCADA
Distribution Feeder Breakers
59.3
58.9
58.5

## Slide 20: Operator Authority
NERC Standards
  PER-001-0
  R1. Each Transmission Operator and Balancing
  Authority shall provide operating personnel with
  the responsibility and authority to implement
  real-time actions to ensure the stable and
  reliable operation of the Bulk Electric System.

## Slide 21: Operator Authority
C. Measures
M1. The Transmission Operator and Balancing Authority provide documentation that operating personnel have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. These responsibilities and authorities are understood by the operating personnel. Documentation shall include:
M1.1 A written current job description that states in clear and unambiguous language the responsibilities and authorities of each operating position of a Transmission Operator and Balancing Authority. The position description identifies personnel subject to the authority of the Transmission Operator and Balancing Authority.
Notes: Main Entry: am·big·u·ous Pronunciation: am-'bi-gy&-w&s Function: adjective Etymology: Latin ambiguus, from ambigere to be undecided, from ambi- + agere to drive -- more at AGENT 1 a : doubtful or uncertain especially from obscurity or indistinctness <eyes of an ambiguous color> b : INEXPLICABLE 2 : capable of being understood in two or more possible senses or ways <an ambiguous smile> <an ambiguous term> <a deliberately ambiguous reply>

## Slide 22: Operator Authority
M1.2 The current job description is readily accessible in the control room environment to all operating personnel.
M1.3 A written current job description that states operating personnel are responsible for complying with the NERC reliability standards.
M1.4 Written operating procedures that state that, during normal and emergency conditions, operating personnel have the authority to take or direct timely and appropriate realtime actions. Such actions shall include shedding of firm load to prevent or alleviate System Operating Limit Interconnection or Reliability Operating Limit violations. These actions are performed without obtaining approval from higher-level personnel within the Transmission Operator or Balancing Authority.

## Slide 23: Operator Authority
TDSP
  Taking those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT Transmission Grid to a secure state in the event of an ERCOT System Emergency.
ERCOT Guides 3.1.5

## Slide 24: Operator Authority
ERCOT Guides 4.2.3, Alert
To minimize the effects on the ERCOT System, all TDSPs will identify and prepare to implement actions, including restoring outaged lines as appropriate and preparation for Load shedding.

## Slide 25: Operator Authority
ERCOT Guides 4.2.4, Emergency Notice
The actions ERCOT takes during a declared emergency will depend on the nature and severity of the situation. If the emergency is the result of a transmission problem that puts ERCOT in an insecure state, then ERCOT will act immediately to return ERCOT to a reliable condition, including instructing Resources to change output and instructing TDSPs to drop Load.

## Slide 26
Summary
Automatic Underfrequency and Undervoltage load shed is triggered by relay action
Automatic load shed occurs at
  59.3
  58.9
  58.5
  .91 PU (3,5 & 8 sec)

## Slide 27
Substitute Block 4 loads for Block 1, 2 & 3 loads to restore system protection
ERCOT Guides, Section 4 details manual load shed procedure and amounts
Operators have the ultimate decision making authority

## Slide 28
References
1 NERC Standards
2 ERCOT Protocols
3 ERCOT Guides
4 ERCOT Operating Procedure Manual Transmission & Security Desk

## Slide 29
Questions
?
?