## Slide 1: Frequency Control
John Dumas

## Slide 2: Objectives
Summarize the ERCOT NERC performance criteria
Describe the new proposed NERC BAL criteria
Discuss the QSE performance metrics
Review frequency related to Operating Guide & Protocol requirements that are placed on Resources

## Slide 3: Defining Frequency Stability
Ability to maintain steady frequency within a nominal range following a disturbance resulting in a significant imbalance between generation and load

## Slide 4: There are three different Interconnections in the US

## Slide 5: What is the relationship between Frequency and Real Power?
ERCOT interconnect approximately 500 – 600 MW loss of generation results in 0.1Hz drop in frequency
Eastern interconnect approximately 3000 MW loss of generation results in 0.1Hz drop in frequency

## Slide 6: Under Frequency Load Shedding
Frequency Threshold | Load Relief
59.3 Hz | 5% of the ERCOT System Load (Total 5%)
58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%)
58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%)

## Slide 7: Generator trip due to frequency
Frequency Range | Delay to Trip
Above 59.4 Hz | No automatic tripping (Continuous operation)
Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes
Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds
Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds
57.5 Hz or below | No time delay required

## Slide 8: Types of Frequency Control
Primary Frequency Control (response time = 5-30 seconds)
  Governors will sense frequency and will automatically adjust turbine valves to increase or decrease thermal or hydro energy to maintain frequency
Secondary Frequency Control (response time = 2-5 minutes)
  Automatic Generation Control (AGC) issues instructions to regulation providers to raise or lower generation in order to maintain frequency at 60 Hz

## Slide 9: Primary Frequency Control depends on Droop setting of a Generator
5% change in frequency = 60 Hz * 0.05 = 3.0 Hz
100% change in generator = Max capability
5% droop of a 300 MW generator
  300 /3.0 = 100 MW/Hz or 10.0 MW/0.1Hz.

## Slide 11: Operating Guide 2.2.5
2.2.5 Turbine Speed Governors
All governors must be placed in-service.
Governor performance tests should be conducted at least every two years and results used in analysis as described in Section 6.2.1, Turbine Governor Speed Regulation Tests. A sample of such tests may be found in Section 6.2.1.2, Example of a Turbine Governor Speed Regulation Test for Mechanical Hydraulic Governor. Every effort should be made to maintain governors with a five percent (5%) droop characteristic.
Primary Frequency Response

## Slide 12: Op Guide 2.2.5 Blocked Governors
There are other elements that can contribute to poor governor response. These include:
Governor dead band. Maximum intentional dead band:
+/- 0.036 Hz.
Valve position limits
Blocked governor operation
Control mode
Adjustable rates or limits
Boiler/turbine coordinated control or set point control action
Automated “reset” or similar control action of the turbine’s MW set point.
Every attempt should be made to minimize the effects of these elements on the governor operation for the duration of all frequency deviations.

## Slide 13: Operating Guide 2.2.3.1
2.2.3.1 Bias Settings
In the Schedule Control Error equation, QSEs shall have bias settings that approximate the measured frequency response characteristic of their On-line Resources. This bias setting should be changed when significant On-line generating capability changes or when their Resources’ frequency response characteristics change. The ERCOT Control Area Authority will check the area frequency response characteristic each time a disturbance qualifies as a measurable event per Section 5.8.2 of the Protocols. Information thus obtained will be used to evaluate ERCOT and QSE bias settings.

## Slide 14
Example of Bad Primary Control

## Slide 15
Example of Good Primary Control

## Slide 16: Market Based Secondary Control
  - Regulation Service
    A service that is used to control the power output of Resources in response to a change in system frequency so as to maintain the target system frequency within predetermined limits.
  Responsive Reserve Service
    Responsive Reserve consists of the daily operating reserves that are intended to help restore the frequency of the interconnected transmission system within the first few minutes of an event that causes a significant deviation from the standard frequency.

## Slide 17: Responsive Reserve On Units
Operating Guide 2.5.2.3
Responsive reserves provided by a QSE shall meet the following requirements:
(1) In no case shall more than twenty percent (20%)of the Net Dependable Capability for any non-Combined Cycle thermal unit be used as Responsive Reserve.
(2) In no case shall more than twenty percent (20%) of the combined Net Dependable Capability for any Combined Cycle Block with one or more CTs or GTs coupled to a Steam Turbine, with their net maximum capability aggregated together, be used as Responsive Reserve.
(3) In no case shall more than twenty percent (20%) of the Net Dependable Capability for any hydro unit with a five percent (5%) droop setting operating as a generator be used as Responsive Reserve.
(4) In no case shall capacity from any Wind unit be used as Responsive Reserve.
Note: Net Dependable Capability is considered HOL in
ERCOT Responsive Reserve Monitoring
20% of HOL

## Slide 18: Responsive Reserve on LAAR
Operating Guide 2.5.2.3
Be capable of interruption by automatic operation of the under-frequency relay(s) set to initiate the interruption whenever system frequency reaches a specific value. The initiation setting of the relay shall not be any lower than 59.7 Hz.;
Have frequency measuring relays with a time delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times.
Be capable of interruption within 10 minutes of receipt of a verbal Dispatch Instruction from ERCOT;

## Slide 19: Maintain Adequate Reserves
5.6.6.1 Emergency Electric Curtailment Plan (EECP)
Step 1 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal to 2300 MW.
  Bring online any units that can start in the time frame of the emergency
  Emergency Energy from the DC Tie
Step 2 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal to 1750 MW.
  Shed LAARs that are providing Responsive Reserve Service
Step 3 — Maintain system frequency at 59.8 Hz or greater
  Shed Firm Load

## Slide 20: Monitoring Secondary Control Performance
6.10.5.3 SCE Monitoring Criteria
  Each QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the equivalent power requirement of any instructed Ancillary Services and other SCE obligation terms including governor response.

## Slide 21
SCE = Actual Generation
+ Load Resource Response to Instructions
– Base Power Schedule
– Sum of any Dynamic Resource Power Schedules
– Expected Governor Response due to frequency of the QSE’s portfolio of Resources (QSE bias in MW/0.1Hz)
– Instructed Ancillary Services
– The signal sent to ERCOT that is estimated in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load (BUL) for Dynamically Scheduled Load
– Fleet/Zonal OOME Dispatch Instruction
SCE Equation

## Slide 22: CPS1 one minute average
The one (1) minute averages of the QSE’s SCE meet the following criteria over the calendar month (commonly referred to as SCPS1), and
The frequency-related parameter, SCPS1, converts a compliance ratio to a compliance percentage as follows:
SCPS1 = (2 – CF) * 100%

## Slide 23: CPS2 – ten minute average
The ten (10) minute averages of the QSE’s SCE meet the following criteria for ninety percent (90%) of the ten (10) minute periods over the calendar month (commonly referred to as SCPS2).
L10 is ERCOT’s L10, presently 106.1008 (varies with ERCOT’s Bias of 489 MW/0.1 Hz)
K = 0.81, Participation Factor calculated by ERCOT for the QSE and sent to the QSE via their RTU.

## Slide 24: NERC Criteria

## Slide 25: ERCOT’s CPS1 Monthly Trend

## Slide 26: 525 Passing 10-Min Interval Percentage Trends

## Slide 27: Balancing Authority ACE Limit (BAAL) – Replaces CPS2
Frequency Relay Limit (FRL)
  59.3 Hz – firm load shedding point
Frequency Abnormal Limit (FAL)
  59.622 Hz – take immediate action to return system frequency above limit
Frequency Trigger Limit (FTL)
  59.932 Hz – must return frequency at or above limit within 30 minutes
  Point chosen based on the ability to withstand loss of the two largest units and stay above FRL
Future NERC Standard

## Slide 28: Summary
Market Based Secondary Control
  Regulation & Responsive Service
  SCE performance monitoring criteria
Primary Control
  Operating Guides require governors to be in service
  PDCWG disturbance report reviews
ERCOT NERC Criteria
  CPS1 & DCS criteria
  Future BAAL standard
Frequency Relays are in place to protect the system

## Slide 29: Questions?