## Slide 1
Lessons Learned from 4/17/06 and changes to EECP
Twenty-Fourth Annual Operations Training Seminar
March - April, 2007
Kent Saathoff, ERCOT

## Slide 2
Introduction
This presentation is intended to describe the events of April 17, 2006 and resulting changes to the ERCOT Emergency Electric Curtailment Plan (EECP) and other ERCOT internal and external procedures

## Slide 3
Objectives
At the completion of this course of instruction you will be able to:
Summarize the events that led up to the 4/17 EECP
List the load forecast issues that may have contributed to the EECP
List the issues that have been addressed to try to alleviate another incident
Explain the procedure changes to the EECP

## Slide 4
Definitions
1 Emergency Electric Curtailment Plan (EECP) – Procedure followed by ERCOT during periods of capacity shortfall
2 Replacement Study – A study done by ERCOT to determine which off-line generating units need to brought on line for reliability purposes
3 Resource Plans – Data provided by QSEs showing what units they plan to have on-line and how they plan to run them
4 Balancing Energy Service (BES) – Available energy bid in by QSEs and deployed by ERCOT to make up the difference between QSE scheduled generation and the short term load forecast

## Slide 5: Definitions (cont.)
5 Non-Spinning Reserve (NSRS) – Off-line generating capacity provided by QSEs that can be brought on line and provide energy within 30 minutes
6 Responsive Reserve – Generating Capacity or Interruptible load provided by QSEs used to help restore the frequency of the interconnected transmission system within the first few minutes of an event that causes a significant deviation from the standard frequency
7 Qualified Scheduling Entity (QSE) – A market participant representing generation and/or load qualified to submit Balanced Schedules and Ancillary Services bids and settle payments with ERCOT.
8 PUCT – Public Utility Commission of Texas
9 SOC – State (Emergency) Operations Center

## Slide 6: Chronological Review of April 17 Events

## Slide 7: April 16 Day Ahead Studies
16:00 April 16 Replacement Study
  Peak load forecast – 49,018 MW
  On-line peak capacity scheduled – 50,661 MW
ERCOT procured additional 2,542 MW capacity for HE 16 and 17 on April 17
01:00 April 17 Replacement Study
  Peak load forecast – 49,591 MW
  On-line peak capacity scheduled – 54,382 MW
  No need seen for additional capacity

## Slide 8: April 17 – EECP
Load tracking above forecast
13:00 Replacement Study
  Peak load forecast – 51,114 MW
  On-line peak capacity scheduled – 55,234 MW
    Included 490 MW that tripped between 12:00 and 13:00
  Resource Plans also showed 1,800 MW off-line capacity available within 30 minutes
  No need seen for additional capacity
Actual demand at 14:00 was 49,194 MW

## Slide 9: Summary of Load/Capacity Outlook
Est. Actual peak
Actual Load

## Slide 10: April 17 13:45 – 15:00
At 13:45, 94% of available Balancing Energy (BES) used – 680 MW off-line reserves (NSRS) deployed
At 13:52 it was found a QSE did not have the 600 MW of available reserve that it was showing
At 14:20 ERCOT had deployed all Regulation Service
At 14:29 243 MW of Responsive Reserve on generation automatically deployed
At 14:36 another QSE showing available reserve was contacted to provide 300 MW
At 15:00 99% of BES used – additional 200 MW NSRS deployed

## Slide 11: 14:00-15:00 Frequency and A/S Deployments

## Slide 12: April 17 15:00 – 16:00
At 15:00 demand was 51,480 MW
At the beginning of the hour frequency and regulation briefly recovered but began to decline again
At 15:14 another QSE showing reserves was asked to increase 200 MW
Frequency continued decline and EECP Step 1 declared at 15:25
  All capacity available to be brought on line and generating
  Arranged schedule for emergency assistance over the DC ties
Frequency continued declining and EECP Step 2 declared at 15:34
  Interruptible loads tripped

## Slide 13: 15:00-16:00 Frequency and A/S Deployments
EECP Step 1
EECP Step 2
222
220 MW
Unit Trip

## Slide 14: April 17 16:00 – 17:00
At 16:00 frequency had recovered to 60 Hz and 150 MW emergency schedule began flowing from the East DC tie
Between 16:01 and 16:07 three units experienced forced outages totaling 1,197 MW capacity
Frequency went below 59.8 HZ
At 16:13 EECP Step 4 was implemented with a hot-line call to Transmission Operators (TOs) asking for 1,000 MW firm load shedding
At 16:17 another unit with 486 MW capacity tripped
At 16:25 EECP Step 3 – Public Appeal for Conservation issued
Frequency recovered to 60 HZ by 16:30

## Slide 15: EECP Step 4 Load Shed Responsibility

## Slide 16: 16:00-17:00 Frequency and A/S Deployments
Unit Trips
1,132 MW
EECP Step 4
EECP Step 3

## Slide 17: April 17 17:00 – 19:20
After 17:00 frequency began to stabilize around 60 Hz and regulation and responsive reserves started coming back
Between 17:32 and 18:10 TOs allowed to restore all firm load
Between 18:21 and 18:29 QSEs allowed to restore interruptible loads
Went back to EECP Step 1 at 18:48 and discontinued DC tie assistance
EECP officially cancelled at 19:20

## Slide 18: Load Forecast Issues
Load forecast was lower than actual loads
  Peak load would have been ~ 53,817 MW if load had not been interrupted (actual was 51,613 MW)
  All-time April peak was 49,280 MW in late April 2002
  April 17 Peak Load forecasts
    49,018 MW @16:00 April 16
    49,591 MW @01:00 April 17
    51,114 MW @13:00 April 17
Why?
  Temperature forecast for DFW area was 5° low (95° vs 100°)
    Accounts for about 1,000 - 1,500 MW error
  Low load forecast for Coast (Houston) area due to corrupted historical data
    Accounts for about 3,000 MW error

## Slide 19: Resource Plan/Available Capacity Issues
The Resource Plan used for the 13:00 April 17 Replacement Study showed 55,283 MW of maximum generating capacity on-line at peak
  Operator saw no problem meeting 51,114 MW forecast
  Would have been enough to cover 53,817 MW load plus 1,150 Responsive Reserve on units, but not by much
  Judgment call on whether to call an Alert if forecast had been 53,817 MW
However, Resource Plans at 13:00 for peak (HE 1700):
  Showed 793 MW that had tripped before 13:00 or was started late (after 16:00)
  Included 1,683 MW capacity that tripped between 15:51 and 16:17

## Slide 20: What if?
Peak load forecast used for the 16:00 April 16 Replacement Study had been 53,817 MW instead of 49,018 MW
  An additional 1,026 MW of capacity off-line at peak April 17 would have been procured
  Given actual unit trips, would have still been in EECP
  Might have avoided Step 4, but would have been close
Units had not tripped or started late
  Might have avoided EECP altogether, but would have been close

## Slide 21
April 17 Follow-up Actions

## Slide 22: Issues Addressed
ERCOT Load Forecast Improvement
Changes to EECP Procedures
Need for improved communication procedures with PUCT, Legislature and Public
Operating Reserves
Desirability of more Interruptible Load
Review Transmission Operator Firm Load shedding Procedures

## Slide 23: Load Forecast Actions
Receiving second forecast from an independent load forecasting service
  Compare to ERCOT forecast
  Investigate reasons for any significant differences
  Decide which one is best to use for Operations decisions
Project underway to make enhancements to ERCOT load forecast model – PR 60084
  Upgrade from v2.2 to v2.5
  Integrate multiple forecast sources into the application
  Provide new methods to ensure data quality and reliability:
    Reasonability limits
    Rate-of-change detection
    Weather data verification

## Slide 24: Improvement in Mid-Term Load Forecasts
Month | Mean Absolute Percent Difference for MTLF run at 16:00 Day Ahead (2005) | Mean Absolute Percent Difference for MTLF run at 16:00 Day Ahead (2006)
January | 5.02 | 4.79
February | 3.47 | 4.81
March | 3.41 | 4.95
April | 3.37 | 5.59
May | 4.21 | 3.59
June | 3.91 | 2.65
July | 5.22 | 2.62
August | 4.86 | 2.09
September | 6.24 | 4.03
October | 4.51 | 3.63
November | 4.53 | 3.28
December | 5.95 | 3.44
Average for year | 4.56 | 3.79

## Slide 25: EECP Procedure Changes
Approved by Board in November
Implemented December 1, 2006
  Bases Notices, Advisories, Alerts and initiation of Steps 1 and 2 of EECP on discounted real-time reserves based on past experience
  Public appeal for conservation can be made Pre-EECP, but no later than EECP Step 2 (when interruptible load is shed)
New Procedures in place for purposes of external communications

## Slide 26: ERCOT External Communications and EECP

## Slide 27: Communications: Pre-EECP and EECP
All EECP Stages
PUC
--Commissioners
--Exec. Director
--Media relations
--Infrastructure/Reliability
--Govt. Relations
Legislative Leadership
Governor’s Office
SOC Hotline
All of the above PLUS…..
News media
All legislators
All market participants & other interested parties
Activate ERCOT.com web page for public updates
Market Participants
-- Subscriber list screened by ERCOT
-- ROS on System Operations “PUCT Daily Report” emails
Early Notifications
ERCOT Officers, Board, & Client Services

## Slide 28
EECP revision changes how reserves are monitored in real time and base notices and EECP implementation on discounted value (Physical Responsive Capability – PRC)
Revised criteria for Non-Spinning Reserve procurement approved by Board in November with Ancillary Services requirements document
  Open second market for additional reserves based on analysis of next day’s Resource Plan
Operating Reserves

## Slide 29: Increased Interruptible Load
ERCOT Staff proposed an Emergency Interruptible Load Program (EILP) to obtain additional interruptible load that can be interrupted after EECP Step 2 and before Step 3 (firm load shedding)
WMS set up a special task force to develop PRR for submittal to PRS
  Four PRRs developed
  Submitted for PRS consideration
  Two PRRs rejected, two PRRs still under consideration
PUCT proceeded with interim rule making

## Slide 30: Firm Load Shedding Procedure
ERCOT sets the amount (MW) of load shed for each Transmission Operator (TO)
Protocols only have general requirement for TOs to keep in mind “the need to protect the safety and health of the community and the essential human needs of the citizens.”
ERCOT conducted survey of TO firm load shedding procedures

## Slide 31: Load Shedding Survey Results
Responses from 15 of 17 TOs (Non-responders ~ 1% of load shed responsibility)
All TOs have established firm load shedding procedures
All TOs rotate customer outages
  Minimum 15 minutes
  Maximum 45 minutes
  Average 18 minutes
Weighted average time to shed load depends on amount requested by ERCOT
  10 minutes for 100 MW
  17 minutes for 1000 MW
All but one TO has procedure for exempting or prioritizing critical customers (that TO has 15 minute rotation)

## Slide 32
References
1 ERCOT Protocols Section 5.6.6.1, Emergency Electric Curtailment Plan
2 ERCOT Operating Guides Section 4.5 Emergency Electric Curtailment Plan

## Slide 33
Questions
?
?