## Slide 1
AUGUST 17, 2006 PEAK DAY POST-MORTEM
OPERATIONS AND PLANNING COMPARISON
LOAD PROJECTION VALIDATION
RESOURCE VARIABILITY
Kenneth A. Donohoo, P.E.
Manager, Transmission Services
System Planning
Operations
ERCOT

## Slide 2
ERCOT Peak Day August 17 2006
Initial Settlement Data by Fuel Type

## Slide 3
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
64,731 MW
63,259 MW
57,376 MW

## Slide 5
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
Wind Generation
342 MW @ peak
2,500 MW Installed Capacity

## Slide 6
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
Hydro Generation
157 MW @ peak
552 MW Installed Capacity

## Slide 7
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
DC Tie
459 MW @ peak
855 MW Installed Capacity

## Slide 8
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
Dispatchable Generation
57,376 MW @ peak
58,573 MW Installed Capacity

## Slide 9
ERCOT AUGUST 17 PEAK DAY
OPERATIONS DATA
Private Network Generation
6,397 MW @ peak
Not Settlement Data
6,419 MW Reported Available

## Slide 10
ERCOT AUGUST 17 PEAK DAY
Operations and Planning Analysis
 | Planning CDR MW | Operations EMS Data MW | Difference from CDR MW | Comments
Generation Available | 58,840 | 57,376 | -1,464 | Differences between NDC and Resource Plan values
Wind | 62 | 342 | 280 | 2.6% in CDR
Hydro | 552 | 157 | -395 | 
DC Tie | 428 | 459 | +31 | 50% in CDR
Private Network | 6,419 | 6,397 | -22 | 
LAAR | 1,112 | 1,150 | +38 | 

## Slide 11
ERCOT AUGUST 17 PEAK DAY
Operations and Planning Analysis
 | Operations EMS Data | 
Load EMS Peak Value | 63,259 | Instantaneous value
Dispatchable Generation | 57,376 | 593 MW Forced Out
Private Network Value | 6,397 | 
Wind Value | 342 | 
DC Tie Capability | 855 | 
Reserve Capacity | 1,711 | 2.7 % of Load
LAAR | 1,150 | 
Total Reserve | 2,861 | 4.5% of Load, Minimum 2,300 MW

## Slide 12
ERCOT AUGUST 17 PEAK DAY
Peak Values
Load EMS Peak Value | 63,259 MW
Initial Settlement 15 Minute | 62,429 MW
Initial Settlement Hour | 62,334 MW

## Slide 13
LOAD FORECAST BACK CAST

## Slide 14
ERCOT AUGUST 17 PEAK DAY
Peak Values

## Slide 16: Weather Zone Forecasting Process
1. Obtain weather and economic variables by weather zone (historic and forecast)
2. Develop regression equations by weather zone describing the historic actual:
  --Monthly Energy
    * Using a different equation for each season
  -- Hourly Load Shape
    * Using a different equation for each season
3. Incorporate forecasted values of economic and normalized temperatures for 2006-2011 by weather zone into monthly energy equation to produce forecasted monthly energy
4. Incorporate normalized temperatures for 2006-2011 by weather zone into monthly energy equation to produce forecasted load shape
5. Produce hourly demand forecast by weather zone by fitting forecasted monthly energy under projected hourly load shape
ERCOT Aggregated
Weather Zone
System Hourly
Load Forecast
Allocate
Energy
Allocate
Energy
Allocate
Energy
ERCOT Aggregated
Weather Zone
Peak and
Energy Forecast
Economic
Data
Weather
Data
Calendar
Data
Weather Zone Forecasted Data
Load
Data
Economic
Data
Weather
Data
Calendar
Data
Weather Zone Historical Data
ERCOT Total System
Summer Hourly
Load Shape Model
by weather zone
ERCOT Total System
Winter Hourly
Load Shape Model
by weather zone
ERCOT Total System
Spring/Fall Hourly
Load Shape Model
by weather zone
ERCOT Winter
Monthly Energy
Model by weather zone
ERCOT Spring/Fall
Monthly Energy
Model by weather zone
ERCOT Summer
Monthly Energy
Model by weather zone
Six Regression Equations by weather zone
Weather Zone Forecasted Data
Weather Zone Historical Data

## Slide 17: Energy Forecast

## Slide 18: Projection of Peak Demand Based Upon Settlement Data

## Slide 19: Weather Zone Forecast Validation Process
Forecast Validation Summary:
1. Use the same historical data up to December 31, 2005, as in the weather normalized forecast, to calculate the coefficients for validating the forecast.
2. Produce the new forecast using actual 2006 temperatures and humidity (as contrasted with normalized weather profiles) but keep the same economic and other non-economic variables as used to produce the weather normalized long-term forecast by weather zone.
Forecast Validation Process:
1. Produce regression equations by weather zone describing the historic actual:
  --Monthly Energy
    * Using a different equation for each season
  -- Hourly Load Shape
    * Using a different equation for each season
2. Incorporate forecasted values for economic variables and actual values for temperatures and humidity for 2006 by weather zone into monthly energy equation to produce forecasted monthly energy
3. Incorporate actual temperatures and humidity for 2006 by weather zone into load shape equation to produce forecasted load shape
4. Produce hourly demand forecast by weather zone by fitting forecasted monthly energy under projected hourly load shape
ERCOT Aggregated
Weather Zone
System Hourly
Load Forecast
Allocate
Energy
Allocate
Energy
Allocate
Energy
ERCOT Aggregated
Weather Zone
Peak and
Energy Forecast
Economic
Data
Actual Temp
Data
Calendar
Data
Weather Zone Forecasted Data
Load
Data
Economic
Data
Weather
Data
Calendar
Data
Weather Zone Historical Data
ERCOT Total System
Summer Hourly
Load Shape Model
by weather zone
ERCOT Total System
Winter Hourly
Load Shape Model
by weather zone
ERCOT Total System
Spring/Fall Hourly
Load Shape Model
by weather zone
ERCOT Winter
Monthly Energy
Model by weather zone
ERCOT Spring/Fall
Monthly Energy
Model by weather zone
ERCOT Summer
Monthly Energy
Model by weather zone
Six Regression Equations by weather zone
Weather Zone Actual and Forecasted Data
Weather Zone Historical Data

## Slide 21
ERCOT AUGUST 17 PEAK DAY
 | MW | Comment
Load EMS Peak Value | 63,259 | 
Initial Settlement 15 Minute | 62,429 | 
Initial Settlement Hour | 62,334 | +1.10% Difference from 2006 Normal Peak Projection
2006 Normal Peak Projection | 61,656 | 
2006 Validation Actual Temp | 62,620 | +0.46% Difference from Initial Settlement Hour
2007 Normal Peak Projection | 63,222 | 
2007 Extreme Peak Projection | 66,027 | 

## Slide 22
EVENTS and NOTICES

## Slide 25
RESOURCE VARIABILITY

## Slide 32
OBSERVATIONS
Hotter than normal summer season and everyone did well!
Available Resources ~65,000 MW
Dispatchable Generation ~57,400 MW
Private Network Resources ~6,400 MW
Planning Load Projection is Hourly (not 15 minute or Instantaneous)
Official Peak 62,334 MW (subject to change based upon settlements)
Validated Planning Load Projection
Resource Variability Significant (much more that load variation)