## Slide 1: Power Plant Operation
ERCOT Operations Seminar
2007

## Slide 2: Purpose Of This Course
Provide overview of generation resources
  Describing various types
  Discuss operational issues

## Slide 3: Objectives
State the purpose of an electrical generator
Discuss advantages and disadvantages of the various prime mover systems.
  State the purpose of a “prime mover”.
  Identify four types of prime movers.
Discuss the principles of operation of each of the various power plant types.
  State the common sources of heat energy used in the generation of electricity.
  Describe the basic heat cycle of a steam turbine power plant.
  List other sources of non-heat energy used in the generation of electricity
Discuss the responsiveness of the various power plant types to dispatch instructions.
Discuss the responsiveness of the various power plant types to load changes.

## Slide 4: Objectives
Discuss the following issues associated with power plants
  Cold Starts
  Hot Starts
  Rotor Soaks, hold time and lockouts (CT)
  Ramp rates and what affects them
  Emissions limitations
  Difficulties with alternate fuel sources
  Run backs
  Tube leaks and why unit shut down rather than continue to run when one occurs
  Turbine and boiler control modes
  Power factors, D curves, Hydrogen cooling and Purity
  ERCOT required test and other in house test, such as, valve test etc.
  Startup and Auxiliary Service transformer functions, Station service requirements

## Slide 5: State the purpose of an electrical generator
Convert Mechanical energy into Electrical energy
  Electromagnetic induction
  Voltage controlled by strength of magnetic field (usually in the rotor) (excitation)
  Frequency controlled by speed of rotation of the rotor
  Power determined by connected load

## Slide 6: How it works.
Strength of magnetic field
Number of conductors
Relative motion

## Slide 7: Purpose Of A “Prime Mover”

## Slide 8: Types Of Prime Movers

## Slide 9: Energy Conversions
Fuel
Steam
Prime Mover
Generator
Load

## Slide 10: Steam-Water Cycle

## Slide 11: Steam Plants
Steam plants can use coal, oil, gas or nuclear fuel
Control of energy conversion reactions are different for different fuels
Different limitations

## Slide 12: Drum-type Boiler Components

## Slide 13: Steam Turbines – good and bad
Good:
Bad:

## Slide 14: Turbine Stages
High Pressure (HP) Turbine
  Main steam
  Exhaust to Reheater
Intermediate Pressure (IP) Turbine
  Reheated steam
  Exhaust to LP Turbine
Low Pressure (LP) Turbine
  IP turbine exhaust
  Exhaust to Condenser

## Slide 16: Condensate/Feedwater

## Slide 17: Auxiliary Systems

## Slide 18: Auxiliary Systems

## Slide 19: Environmental Limitations

## Slide 20: Fuel Limitations (Coal)

## Slide 21: Fuel limitations (Natural Gas)

## Slide 22: Maintenance Limitations
Auxiliary equipment out of service
  Heat cycle equipment
  Pulverizers or oil pumps
  ID or FD fans
  Circulating water pumps

## Slide 23: Operating Limitations
Chemicals in feedwater
Poor equipment thermal performance
High vibration on rotating equipment
High condenser backpressure
  Vacuum leaks
  Dirty condenser waterboxes

## Slide 24: Steam Plant Response to Dispatch

## Slide 25: Combustion Turbine

## Slide 26: Combustion Turbine

## Slide 28: CT Advantages

## Slide 29: CT Disadvantages

## Slide 30: Environmental Considerations

## Slide 31: CT Response to Dispatch

## Slide 32: Combined Cycle Units

## Slide 34
Notes: 1-ON-1 Combined-Cycle

## Slide 35: Combined Cycle Advantages

## Slide 36: Combined Cycle Advantages

## Slide 37: Combined Cycle Dispatch Response

## Slide 38: PWR Nuclear (Single Loop)

## Slide 39: Reactor Operation

## Slide 40: Nuclear Limitations
Slow response to large changes in load
Most cost-efficient when running at full power output
Large staff required (not just operations)
  Regulatory requirements
  Security
  Maintenance
Waste management

## Slide 41: Nuclear Advantages

## Slide 42: Nuclear Response to Dispatch
Preferred last resort for balancing down (done by OOME)
Automatic operation limited by license requirements

## Slide 43: Water Turbine (HydroElectric)
Hydro Generating Plants
Generating capability depends on two factors:

## Slide 44: Hydro advantages
Minimal fuel cost
Lends itself to automatic operation

## Slide 45: Hydro disadvantages

## Slide 46: Hydro Operation
Gross Power (kW) =
0.0848 * Flow (ft3/sec * gross head (ft)
Example: 0.0848 * 75 * 500 = 3168.75 kW

## Slide 47: Hydro Response
Load reduction – fairly quick response
Load increase – fairly slow response (safe increase in water flow)
Response limited by available head (penstock pressures)

## Slide 48: Windmill

## Slide 49
From www.awea.org/faq/tutorial/wwt_basics.html

## Slide 50: Wind power, the good and the bad
Good:
Bad:

## Slide 51: Wind Response to Dispatch
Not reliable for increased output instructions
Can quickly respond to decreased output instructions

## Slide 52: Diesel Engine

## Slide 53: Other energy sources
Geothermal
Tidal
Solar
Landfill gas

## Slide 54: Questions?