## Slide 1: Block Load Transfers (BLTs) and other Important Stuff

## Slide 2
Block Load Transfers (BLTs)

## Slide 3: Block Load Transfer
What is a Block Load Transfer (BLT)?
The transfer of load normally located in the ERCOT Control Area to a Non-ERCOT Control Area
AND
The transfer of load from Non-ERCOT Control Areas to the ERCOT Control Area
Note:
All transfers between ERCOT and Non-ERCOT Control Areas must be dead-line pickups.

## Slide 4: Block Load Transfer
Requirements for Registering a BLT
If BLT is to block ERCOT load into a Non-ERCOT control area:
  Create an ERCOT registered Resource Entity
  Resource Entity / QSE affiliation executed
  Complete BLT Registration form (assign RID)
  Metering design documentation provided to ERCOT
If BLT is to block Non-ERCOT load into ERCOT control area:
  Create an ERCOT registered Load Serving Entity (LSE)
  LSE / QSE affiliation executed
  Complete BLT Registration form (assign ESI ID)
  TDSP associated with BLT point responsible for the creation and maintenance of BLT ESI-ID
Note: Some BLT’s can be bi-directional and therefore must meet the requirements for transferring load in either direction

## Slide 5: Block Load Transfer
Conditions for Implementation
From ERCOT to Non-ERCOT Control Area
Under Alert or EECP Conditions
Under specific Dispatch Instruction from ERCOT and permission of the affected Non-ERCOT Control Area
From Non-ERCOT Control Area in to ERCOT
When Non-ERCOT Control Areas experience certain transmission contingencies or short supply conditions
Under specific Dispatch Instruction from ERCOT
Important Note:
The necessary Market Participant agreements, metering, and ERCOT settlement systems are to be in place prior to implementation of any BLT

## Slide 6: Block Load Transfer
Helpful Preparation Tips
(prior to impending event or hurricane season)
Start discussions with adjacent TDSPs outside ERCOT control areas
Have copies of transmission and distribution one-lines available
Contact your ERCOT Client Representative and communicate possible need for creating a BLT to help in storm restoration plans

## Slide 7
Load Participation Update

## Slide 8: Demand Response: Present
In the restructured market, interruptible tariffs have been replaced by market-based programs
  Load Acting as a Resource (LaaR)
  Balancing Up Load (BUL)
    No current subscribers
  Price-responsive load (voluntary)
    Total participation & strike prices unknown
Resource Type | Service Provided | Requirements
Load Acting as a Resource (LaaR) | Various Ancillary Services | IDR Meter Telemetry Qualification
Balancing Up Load (BUL) | Balancing Energy Services (Up) | IDR Meter Qualification
Voluntary Load Response | Curtailment or reduction in response to market prices or other factors | Metering and/or curtailment technology defined in contract with LSE & QSE

## Slide 9: LaaR Requirements
In ERCOT the services a LaaR can provide is based on their qualification.
3 Types of Qualification for LaaRs
  Interruptible Load (ILD)
  Under-frequency Load (UFR)
  Controllable Load (CLD)

## Slide 10: LaaR Requirements
Type | Services | Requirements
In ERCOT the services a LaaR can provide is based on their qualification.
ILD (Interruptible) | NSRS | IDR Settlement Meter Telemetry MW Load Breaker Status Response Value (MWs) Complete qualification test Respond within 30 minutes of dispatch instruction

## Slide 11: LaaR Requirements
Type | Services | Requirements
In ERCOT the services a LaaR can provide is based on their qualification.
UFR (Under-frequency) | NSRS RRS RPRS BES | IDR Settlement Meter Under-frequency Relay (59.7 hz) Telemetry MW Load Breaker Status UFR Status Response Value (MWs) Complete qualification test Respond within 10 minutes of dispatch instruction

## Slide 12: LaaR Requirements
Type | Services | Requirements
In ERCOT the services a LaaR can provide is based on their qualification.
CLD (Controllable) | NSRS RRS RGS Up RGS Down | IDR Settlement Meter “AGC Like” Control Able to respond automatically to frequency changes similar to governor action Telemetry MW Load Response Value (MWs) Complete qualification test

## Slide 13: LaaR Update

## Slide 14: LaaR Update

## Slide 15: Market Clearing Prices for RRS Service

## Slide 16: LaaR Update
Notes:
Value only represents that procured in the AS Market and excludes all self arranged quantities.
Hurricane effect on prices
Overall cost reduction to the market from 2005 reflects significant shift to self arranging

## Slide 17: LaaR Deployments
LaaRs Providing RRS can be deployed:
  Automatic trip based on UFR settings (2 trip points)
  Verbal dispatch by ERCOT during EECP event (deployed as block)
  Verbal dispatch by ERCOT during low frequency event reportable to NERC (deployed as block)
  Verbal dispatch by ERCOT to solve a local congestion issue (location-specific)
LaaRs were deployed three times in 2006:
  April 17 EECP Event (Manually Deployed)
  Oct. 3 Low frequency Event (Manually Deployed)
  Dec. 22 Under-frequency Event (Automatic & Manually Deployed)

## Slide 18
LaaR Deployment Summary

## Slide 19: LaaR RRS Deployment

## Slide 20
Controllable Load Update

## Slide 21: Controllable Load Resource
What is a Controllable Load Resource?
Load Resource capable of providing Regulation Service by controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately responds proportionally to frequency changes (similar to generator governor action).

## Slide 22: Controllable Load Resource
Status Summary
Initiated pilot project in October 2006
To limit potential disruption to ERCOT frequency control only one Load Resource and was allowed to participate up to 10 MWs
Pilot concluded successfully in early January 2007
January PUCT Open Meeting
  ERCOT directed to open service up to all participants
ERCOT estimates up to 150 MWs of load could participate as Controllable Load

## Slide 23: Controllable Load Resource
Pilot Limitations:
Meet all requirements for participation as a LaaR
  IDR meter
  Real Time telemetry at the controllable load installed and tested
  Successfully complete qualification test
Able to respond proportionately to frequency changes (similar to generator governor action
Capable of reducing or increasing consumption in response to dispatch instruction (similar to AGC)
Site has to “look”, “act”, and “smell” like a generation resource (eg; power flow at point of the settlement meter shall be a net generation point while providing services as a controllable load)
Need to bid in as a “GEN” type and not “CLD” Resource (for RRS only)
Resource agrees to waive its right to receive any resource-specific premium payments that would result from a unit specific instruction (OOME)

## Slide 24: Controllable Load Resource
Controllable Load can provide:
Regulation Up, Regulation Down, or both
Responsive Reserve Service
Note:
Any capacity from a Controllable Load providing RRS would not be included in the ERCOT established limit for LaaRs providing RRS.

## Slide 25: Controllable Load Resource

## Slide 26
Load Participation In RPRS Update

## Slide 27
Status Summary
Replacement Reserve Service (RPRS) implemented in March 2006
LaaRs were disabled from providing RPRS due to some network mapping issues
Mapping issues resolved and LaaRs enabled on February 2007

## Slide 28: LaaR Participation in RPRS
Things a QSE should know/pre ….
Deployment
  Electronically Transmitted via XML
  Hours of Capacity Dispatch included
What does a QSE do when RPRS is procured from the QSE?
  Receive and XML Message
  Update Resource Plan Accordingly
  Add entire capacity of RPRS Resource into Up Balancing Energy Bid Stack
  Ensure Resource Ready for dispatch for specific hours

## Slide 29: Changes Coming down the Road
In 2009 ERCOT changing from existing Zonal Market to a Nodal Market

## Slide 30: Questions?
ON
OFF