## Slide 1
Impact of Transmission System Voltage

## Slide 2
Introduction
This presentation will provide an understanding of the role that voltage constraints play in maintaining system reliability. Discussion will include contingencies, planning requirements, the creation of the voltage profile, and risks associated with operating outside of voltage limits.

## Slide 3
Objectives
At the completion of this course of instruction you will:
Identify the different contingency categories and how they affect system security;
Identify the significance of the ERCOT voltage profile and how it gets created;
Identify how ERCOT, QSEs, and transmission companies work together to maintain system voltage.

## Slide 4
What is n-1
‘n’ is the total number of transmission “elements” in the system
‘n-1’ is the total system with one element out of service
  The event (unplanned) of this element going out of service is called a “contingency”
  In the real-time environment it is the next element

## Slide 5
Planning Criteria
NERC/ ERCOT
  ERCOT Operating Guides – Section 5
  4 categories of operating conditions:
    A, B, C, D
TDSPs can have their own planning criteria in addition to the NERC and ERCOT criteria

## Slide 6
Planning Criteria
Category A - all elements in service
  Transmission elements within their continuous (or normal) ratings
  Voltage within normal limits
  System stable and no loss of load

## Slide 7
Planning Criteria
Category B – n-1 where the “minus one” is:
    Generation unit
    Transmission line
    Transmission transformer
    Generation unit and either a transmission line or transformer*
    Double circuit transmission lines sharing towers for more than 0.5 mile*
  Transmission elements within their emergency ratings
  Voltage within emergency limits
  System stable and no loss of load

## Slide 8
Planning Criteria
Category C – n-1 where the “minus one” is a fault on:
    Bus section
    Breaker
Or Category B event with delayed clearing
Or two n-1 events
  Transmission elements within their emergency ratings
  Voltage within emergency limits
  System stable/ only planned and controlled loss of load

## Slide 9
Planning Criteria
Category D – extreme contingency event
  May involve substantial loss of customer demand and generation in a widespread area
  Requires documentation of procedures to mitigate the extent and effects of such an event

## Slide 10
What is Voltage
Voltage – a measure of the potential energy of an electric field to cause an electric current in an electrical conductor.
  1 volt =amount of force needed to push 1 amp through 1 ohm

## Slide 11
Voltage in ERCOT
Referenced in kV and pu
Responsibility of transmission companies, generation companies, and ERCOT – working together

## Slide 12
Planning Standards for Voltage Limits
Entity | Normal Pre-Contingency | Emergency Post-Contingency
AEP | .95pu | .90pu (lower if customer protected by LTC)
AEN | .95pu | .90pu
CNP | .95pu 1.01pu (STP) | .95pu (Category B) .92pu (Category C) 1.01pu (STP)
CPS | .95pu | .93pu (probable disturbances) .90pu (extreme disturbances)
TNMP | .95pu | .90pu
TXU | .95pu (345-kV buses) .94pu (138-kV and 69-kV buses) .99pu (Comanche Peak nuclear) | -5% ∆voltage from normal (345-kV) -5% ∆voltage from normal (69 & 138) .98pu (Comanche Peak nuclear)
ERCOT | .95pu | .95pu
Table compiled from Planning Criteria posted on ERCOT System Planning Website

## Slide 13
Voltage Stability
Ability of power system to maintain steady voltage following a disturbance
ERCOT uses VSAT software tool to analyze voltage stability
TDSPs have option of using under-voltage load shed (UVLS) as a safety net

## Slide 14
Voltage Profile
Set of voltage set points for all generators in ERCOT
ERCOT posts seasonally per protocol sections 6.5.6 and 6.5.7
  Also see Operating Guides section 2.10

## Slide 15
Voltage Profile
Steady State WG seasonal base case
Program performs n-1 analysis for all ERCOT
Program lists all n-1 voltage violations
Transmission Owners “tune” model
Adjust cap banks/ reactors/ transformer taps/ FACTS devices
Adjust generator set points
ERCOT posts final list of generator set points

## Slide 16
Voltage Profile
Generators “should” operate at their profile set point
  Compliance measure is ± 2%
TDSPs and ERCOT responsible for leveling reactive output of generators based on size

## Slide 17
Powerworld Contingency Demonstration

## Slide 18
Questions
?
?