## Transfer Analysis
2008 CSC Transfer Analysis
CSC | Transfer change from base case (MW) | Limiting Element | Contingency | CSC/ CRE Relation
W-N | 687.7 | Willow Creek-Parker 345-kV line | Graham-Parker/ Graham-Benbrook 345-kV double circuit | LE is CRE; Con is CSC
W-N | 1371.7 | Benbrook-Parker 345-kV line | Parker-Roanoke/ Parker-Eagle Mountain 345-kV double circuit | LE is CRE
W-N | 1409.3 | Willow Creek-Parker 345-kV line | Jacksboro-West Denton 345-kV line | LE is CRE; Con is CRE
W-N | 1577.2 | SAPS-Yellowjacket 138-kV line | Graham-Sweetwater/ Graham-Long Creek 345-kV double circuit | Con is CRE
W-N | 1606.4 | Barton-Oran 138-kV line | Graham-Parker/ Graham-Benbrook 345-kV double circuit | LE is CRE; Con is CSC
W-N | 1948 | Oklaunion-Fisher Road 345-kV line | Graham-Sweetwater/ Graham-Long Creek 345-kV double circuit | LE is CRE; Con is CRE
W-N | 1980.9 | Willow Creek-Parker 345-kV line | Graham-Parker 345-kV line | LE is CRE; Con is part of CSC
W-N | 2002.8 | Murray-Graham 138-kV line | Graham-Sweetwater/ Graham-Long Creek 345-kV double circuit | LE is CRE; Con is CRE
W-N | 2007.6 | Graham-Parker 345-kV line | Willow Creek-Parker 345-kV line | LE is part of CSC; Con is CRE
W-N | 2139.5 | Paint Creek-Murray 138-kV line | Graham-Sweetwater/ Graham-Long Creek 345-kV double circuit | LE is CRE; Con is CRE
W-N | 2164.2 | Barton-Oran 138-kV line | Benbrook-Parker/ Benbrook-Graham 345-kV double circuit | LE is CRE; Con is part CSC/ part CRE
W-N | 2188.9 | Barton-Oran 138-kV line | Parker-Roanoke/ Parker-Eagle Mountain 345-kV double circuit | LE is CRE
W-N | 2232.9 | Graham-Parker 345-kV line | Graham-Benbrook 345-kV line | LE is part of CSC; Con is part of CSC
W-N | 2360.1 | Long Creek-Graham 345-kV line | Oklaunion-Fisher Road-Bowman 345-kV line | LE is CRE; Con is CRE
W-N | 2395.1 | Graham-Parker 345-kV line | Benbrook-Parker/ Benbrook-Graham 345-kV double circuit | LE is part of CSC; Con is part CSC/ part CRE
W-N | 2589.6 | Putnam-Leon 138-kV line | Graham-Sweetwater/ Graham-Long Creek 345-kV double circuit | Con is CRE
S-N | 456.6 | Butler-Elgin 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
S-N | 1783.7 | Sim Gideon-Butler 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
S-N | 1828.3 | Decker-McNeil 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
S-N | 2219 | Gilleland-McNeil 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
S-N | 2638.2 | Austrop-Sandow 345-kV line | Austrop-Sandow 345-kV line | LE is CRE; Con is CRE
S-N | 3302.1 | Wells Branch-Round Rock S 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
N-S | -60.5 | Temple Pecan Creek-Temple 138-kV line | Temple-Temple Pecan Creek/ Temple-Lake Creek 345-kV double circuit | LE is CRE; Con is CRE
N-S | -51.9 | Waco W-Wacowood 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | -38.3 | Tradinghouse-Lake Creek 345-kV line, ckt 2 | Tradinghouse-Lake Creek/ Tradinghouse-Temple Pecan Creek 345-kV double circuit | LE is CRE; Con is CRE
N-S | 293.3 | Lake Creek-Temple Pecan Creek 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | LE is CRE; Con is CRE
N-S | 340.3 | Lake Creek-Temple 345-kV line | Tradinghouse-Temple Pecan Creek 345-kV line | LE is CRE; Con is CRE
N-S | 354.4 | Temple Pecan Creek 345/138-kV autotransformer | Temple-Temple Pecan Creek/ Temple-Lake Creek 345-kV double circuit | Con is CRE
N-S | 384.8 | Tradinghouse-Temple Pecan Creek 345-kV line | Lake Creek-Temple 345-kV line | LE is CRE; Con is CRE
N-S | 395 | Lake Creek-Temple 345-kV line | Tradinghouse-Lake Creek/ Tradinghouse-Temple Pecan Creek 345-kV double circuit | LE is CRE; Con is CRE
N-S | 440.1 | Wacowood-Woodway Tap 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 440.1 | Woodway Tap-Waco Atco 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 551.7 | Temple-Bell County 138-kV line | Temple-Sandow 345-kV double circuit | Con is CSC
N-S | 757.4 | Whitney-Cayote 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 788.4 | Cayote-Bosque 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 852.5 | Sandow-Salty 138-kV line | Austrop-Sandow 345-kV double circuit | LE is CRE; Con is CRE
N-S | 882.7 | Salty-Thorndale 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
N-S | 961.4 | Waco Atco-Spring Valley Tap 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 968.3 | Bell County-Salado 138-kV line | Temple-Sandow 345-kV double circuit | Con is CSC
N-S | 969.2 | Thorndale-Taylor 138-kV line | Austrop-Sandow 345-kV double circuit | Con is CRE
N-S | 1055.1 | Spring Valley Tap-McGregor Tap 138-kV line | Tradinghouse-Temple Pecan Creek/ Lake Creek-Temple 345-kV double circuit | Con is CRE
N-S | 1056.1 | Lake Creek-Temple 345-kV line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | LE is CRE
N-H | 937.2 | Gibbons Creek-Obrien 345-kV line | Jewett-Tomball/ Roans Prairie-Kuykendahl-King 345-kV double circuit | LE is part of CSC; Con is CRE
N-H | 1656.9 | Tradinghouse-Temple Pecan Creek 345-kV line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | Con is part CSC part CRE
N-H | 1844 | Roans Prairie-Kuykendahl 345-kV line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | LE is CRE; Con is CSC
N-H | 2014.8 | Jewett-Tomball 345-kV line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | LE is CRE; Con is CSC
N-H | 2174.9 | Jewett-TH Wharton 345-kV line | Jewett-Tomball/ Roans Prairie-Kuykendahl-King 345-kV double circuit | LE is part of CSC; Con is CRE
N-W | 3134.1 | Hasse-Dublin 138-kV line | Comanche Peak-Comanche 345-kV line | Con is CRE
N-W | 3163.9 | Comanche Tap-Hasse 138-kV line | Comanche Peak-Comanche 345-kV line | Con is CRE
N-W | 3439.8 | Comanche-Comanche Tap 138-kV line | Comanche Peak-Comanche 345-kV line | Con is CRE
N-W | 3716.6 | Barton-Oran 138-kV line | Graham-Parker/ Graham-Benbrook 345-kV double circuit | LE is CRE; Con is CSC
N-W | 3854.1 | Barton-Oran 138-kV line | RW Miller-Stephenville 138-kV line | LE is CRE
N-W | 3881.9 | Dublin-Stephenville 138-kV line | Comanche Peak-Comanche 345-kV line | Con is CRE
N-W | 3891.6 | Graham-Barton 138-kV line | Graham-Parker/ Graham-Benbrook 345-kV double circuit | LE is CRE; Con is CSC

## Congestion Analysis
2008 CSC Related Congestion from 2006 5-Year Plan (Sorted by Shadow Price)
MonitoredFrom Bus | MonitoredTo Bus | MonitoredVoltage | Capacity | N-X | DirectionF:ForwardR:Reverse | Percent ofCongestion(%) | ContingencyLine1:From Bus | ContingencyLine1:To Bus | ContingencyLine1:Voltage | ContingencyLine2:From Bus | ContingencyLine2:To Bus | ContingencyLine2:Voltage
PETERS 9 | PETERS 8 | 69 | 42 | N-2 | R | 3.28 | TOMBAL 5 | JEWETT N | 345 | KING 5 | KUYDAL 5 | 345
BUTLER13 | ELGIN 13 | 138 | 143 | N-2 | F | 14.57 | AUSTRO34 | SANDOW | 345 | AUSTRO34 | SANDOW | 345
LAKE CRK | TEMP PEC | 138 | 186 | N-2 | F | 8.86 | T HOUSE | TEMP PEC | 345 | LAKE CRK | TEMP SS | 345
ELGIN SS | TAYLOR | 138 | 127 | N-1 | F | 0.02 | SANDOW | SALTY M | 138
OBRIEN 5 | GIBCRK B | 345 | 1484 | N-2 | R | 0.39 | TOMBAL 5 | JEWETT N | 345 | KING 5 | KUYDAL 5 | 345
MCNEIL13 | GILLEL13 | 138 | 191 | N-2 | F | 0.17 | AUSTRO34 | SANDOW | 345 | AUSTRO34 | SANDOW | 345