## Slide 1: Information Technology Service Availability Metrics
March 2008

## Slide 2: Summary
IT infrastructure and production change problems caused March IT performance to be below service level expectations
Impacts to the market included delayed retail transaction processing, generation of duplicate transactions, delayed data extract & report posting, and outages outside of scheduled maintenance windows
Efforts are complete or underway to remediate these problems and improve the IT infrastructure to avoid future problems in this area

## Slide 3: Summary
Retail Transaction Processing Outages & Delays
  Causes:
    Failed Production Release
      SCR-745 related production implementation caused delays and failures resulting in the decision to rollback to pre-implementation state
    Storage Hardware Failures
      Multiple storage hardware failures caused unplanned outages, compounding transaction processing delays already slowed by the failed production release
    Human Error
      During troubleshooting efforts, a computer operator started a session of a process that was already running, causing significant duplicate transactions to be generated and requiring the manual cleanup of transactions
  Resolution:
    Failed Production Release
      Due to slow performance and crashes, an outage outside of the standard maintenance windows was utilized to rollback to pre-implementation state
      Technical analysis and discussions with TDTWG are ongoing to determine next steps regarding this phase of SCR-745
    Storage Hardware Failures
      Project to replace aged hardware has been in progress since late ’07 and is scheduled for implementation during the first weekend in May
    Human Error
      Education and training
      Operating procedure revisions to prevent future occurrences

## Slide 4: Summary
MarkeTrak slow system performance and failures
  Causes:
    Application instability and limitations:
      Single vs. multi-threading processing abilities
      HTTP sessions management capabilities
    Storage hardware failures
      When the SAN fails, the MarkeTrak application fails as well
  Resolution:
    Application instability and limitations:
      Version upgrade that will address these issues has been in process since late ’07, two versions of the upgrade have failed ERCOT testing and have had to be returned to the vendor for fixes
      Most recent version upgrade is in ERCOT testing and if successful it will be promoted to production during the May release
    Storage hardware failures
      Project to replace aged hardware has been in progress since late ’07 and is scheduled for implementation during the first weekend in May

## Slide 5: Summary
Wholesale Batch, Data Extracts & Reports Delays
  Causes:
    Storage hardware failures
      Failures delayed batch processing which in turn delayed reports and extracts
    Human errors
      Data cleanup activities inadvertently caused incorrect data to be generated during the batch process, the remediation efforts required the backout and rerun of three operating days, much of which had to be performed manually
      Permissions not granted properly during the March retail release, causing files to not be able to flow where they needed to for report generation
  Resolution:
    Storage Hardware Failures
      Project to replace aged hardware has been in progress since ’07 and is scheduled for implementation during the first weekend in May
    Human errors
      Education and training

## Slide 6: 2008 Net Service Availability
3

## Slide 7: March 2008 Net Service Availability
4

## Slide 8: Retail Transaction Processing Availability Summary
5

## Slide 9: TML Availability Summary
6

## Slide 10: MarkeTrak Availability Summary
7