## Slide 1: CenterPoint Energy Rothwood Substation Project
May 8, 2008
Technical Advisory Committee
Jay Teixeira
Manager, Regional Planning

## Slide 2: Description of Recommendation
Technical Advisory Committee
May 8, 2008
Build Rothwood 345/138 kV substation. Add 800 MVA auto looping 345 kV ckt 74 Kuykendahl tap - King and 138 kV ckt 66 Tomball - Westfield where 345 kV ckt crosses Rayford tap section. Loop in only one of the tap sections. Convert Rayford into a loop tap substation
Cost: $21,500,000
Upgrade ckt 66 Tomball - Rothwood - Rayford to a minimum continuous rating of 360 MVA and minimum emergency rating of 440 MVA
Cost: $1,500,000
TOTAL COST: $23,000,000
Scheduled in-service prior to Summer 2010

## Slide 3: Project Need - Reliability Analysis
Technical Advisory Committee
May 8, 2008
Need for project to meet reliability criteria was determined during work on 2007 Five-Year Plan
Contingency of Tomball to Jewett (Singleton)/King to Kuykendahl to Tomball 345kV lines results in overloads on North Belt to Westfield and Humble to Treaschswig that cannot be resolved through redispatch
Unserved
energy
Contingency
Overload
Element

## Slide 4: Project Need - Reliability Analysis
Rothwood Substation project eliminates overloads and unserved energy for same contingency.

## Slide 5: Project Need - Reliability Project Options
Technical Advisory Committee
May 8, 2008
Option 1  | 
Reconductor North Belt-Westfield 138 kV line | 
Reconductor Humble to Treaschwig 138 kV line | 
Total Cost | $ 8,180,000
Rothwood Substation Project (2013) | $23,000,000
Total Cost | $31,180,000
Option 2  | 
Rothwood Substation Project (2010) | $23,000,000
Total Cost | $23,000,000

## Slide 6: Discussion of Options
Both options meet reliability requirements
The Rothwood Substation additionally resolves congestion on the Tomball autos ($2.7M in annual production cost savings) which is not resolved by reconductor projects alone
Rothwood would eventually be needed for reliability in Option 1 (shown as needed in 2013).
Deferral of Rothwood substation by three years in Option 1, with deferral of the associated production cost savings, does not offset the additional cost of the reconductor projects.

## Slide 7: Stakeholder Review
Technical Advisory Committee
May 8, 2008
The Stakeholder review period for this project was held in April 2008
There were no dissenting comments on this package

## Slide 8: ERCOT Support for the Project
Technical Advisory Committee
May 8, 2008
ERCOT will be requesting that the Rothwood Substation project be endorsed by the ERCOT Board Of Directors.

## Slide 9
Questions?