| NPRR Number | 119 | NPRR Title | Resource Limit Calculator |
| --- | --- | --- | --- |
| Date Posted |  | March 27, 2008 |  |
| Protocol Section(s) Requiring Revision (Include Section No. and Title) |  | 6.5.7.2, Resource Limit Calculator |  |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) |  | Normal |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) changes the Low Dispatch Limit (LDL) calculation to ensure that the LDL and High Dispatch Limit (HDL) limit sent to the Security Constrained Economic Dispatch (SCED) do not exceed the High Sustained Limit (HSL) under any circumstance. |  |
| Reason for Revision |  | When the output MW of a Resource exceeds its telemetered HSL for a short time (e.g. governor response) SCED will attempt to dispatch the Resource above its HSL. Modifying the LDL calculation with a final check will ensure that the LDL and HDL limits calculated by the Resource Limit Calculator (RLC) and sent to SCED do not exceed the HSL under any circumstance. |  |
| Overall Market Benefit |  | Unknown. |  |
| Overall Market Impact |  | Unknown. |  |
| Consumer Impact |  | Unknown. |  |
| Credit Implications (Yes or No, and summary of impact) |  | No credit impacts are anticipated. |  |
| Reason for Revision (from Transition Plan Task Force (TPTF) Charter Scope) |  | (1) Revisions resulting from Commission orders; (2) Clarifications of Protocol language that do not change the intent or technical specifications of the Protocols; (3) Correction of technical errors or processes that are found to not be technically feasible; (4) Revisions to the Protocols necessary to implement the results of the value engineering analysis or to otherwise avoid severe cost impacts; or (5) Other (describe): |  |
| TPTF Review (Yes or No, and summary of conclusion) |  | No – This NPRR is scheduled for review during the March 31-April 1, 2006 Transition Plan Task Force (TPTF) meeting. |  |

Quantitative Impacts and Benefits

| Assumptions | 1 | Facilitates compliance with NERC Reliability Standards |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown | Unknown |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Unknown | Unknown |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Kenneth McIntyre |
| E-mail Address | kmcintyre@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3969 |
| Cell Number |  |
| Market Segment | n/a |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Nieves López |
| E-Mail Address | nlopez@ercot.com |
| Phone Number | (512) 585-0927 |

Proposed Protocol Language Revision

6.5.7.2	Resource Limit Calculator

(1)	ERCOT shall calculate the HASL, LASL, SCED Up Ramp Rate (SURAMP), SCED Down Ramp Rate (SDRAMP), HDL and LDL within four seconds after a change of the Resource-specific attributes provided as part of the QSE’s SCADA telemetry under Section 6.5.5.2, Operational Data Requirements.  The formulas described below define which Resource-specific attributes must be used to calculate each Resource limit.  The Resource limits are used as inputs into both the SCED process and the Ancillary Service Capacity Monitor as described in Section 6.5.7.6, Load Frequency Control.  These Resource limits help ensure that the deployments produced by the SCED and Load Frequency Control (LFC) processes will respect the commitment of a Resource to provide Ancillary Services as well as individual Resource physical limitations.

(2)	The figure below illustrates how the Resource Limit Calculator determines the Resource limits for both Generation and Load Resources:

LSL

HSL

Time

HSL

-

LSL

-

0

LASL

-

HASL

-

Generation

Increase

Generation

Decrease

Ancillary

services

provided: Reg

Down

Ancillary sServices

provided: Reg Up,

Responsive, Non

-

Spin

(as applicable)

Current

Telemetry

HDL

LDL

Ramp

Rate

5 Minutes

HSL=

-

LPC

LSL=

-

MPC

LASL

-

HASL

-

Consumption

Decrease

Consumption

Increase

Current load

Telemetry

Ancillary services

provided: Reg Down

Ancillary sServices

provided: Reg Up,

Responsive

, Non-Spin

Generation

5

-

30

Minutes

Load Resources

Sign Convention for Load Resources

Normal Load

fluctuation

Quantity

Offer Curve Generation

LSL

HSL

-

-

0

-

-

Generation

Increase

Generation

Decrease

-

Spin

Ramp

Rate

5 Minutes

-

-

-

-

Consumption

Decrease

Consumption

Increase

5

-

30

-

-

0

-

-

Generation

Increase

Generation

Decrease

-

Spin

Ramp

Rate

5 Minutes

-

-

-

-

Consumption

Decrease

Consumption

Increase

5

-

30

Price

(3)	High Ancillary Service Limit (HASL) is calculated as follows:

HASL	=	Max (LASL, (HSLTELEM – (RRSTELEM + RUSTELEM + NSRSTELEM)))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit |
| HSLTELEM | High Sustained Limit provided via telemetry – per Section 6.5.5.2 |
| LASL | Low Ancillary Service Limit |
| RRSTELEM | Responsive Reserve Ancillary Service Schedule provided by telemetry |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry |
| NSRSTELEM | Non-Spin Ancillary Service Schedule provided via telemetry |

(4)	Low Ancillary Service Limit (LASL) is calculated as follows:

LASL	= 	LSLTELEM + RDSTELEM

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit |
| LSLTELEM | Low Sustained Limit provided via telemetry |
| RDSTELEM | Reg-Down designation provided by telemetry |

(5)	For each Generation Resource, the SURAMP is calculated as follows:

SURAMP	= 	 RAMPRATE– (RUSTELEM / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED up ramp rate |
| RAMPRATE | Normal Ramp Rate when RRS is not deployed or when the subject Resource is not providing RRS. Emergency Ramp Rate for Resources deploying RRS |
| RUSTELEM | Reg-Up designation provided by telemetry |

(6)	For each Generation Resource, the SDRAMP is calculated as follows:

SDRAMP	= 	NORMRAMP – (RDSTELEM / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED down ramp rate |
| NORMRAMP | Normal Ramp Rate |
| RDSTELEM | Reg-Down designation by Resource provided via telemetry |

(7)	For Generation Resources, HDL is calculated as follows:

HDL	= 	Min (POWERTELEM + (SURAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit |
| POWERTELEM | Gross or net real power provided via telemetry |
| SURAMP | SCED up ramp rate |
| HASL | High Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

(8)	For Generation Resources, LDL is calculated as follows:

LDL	= 	Min{Max (POWERTELEM - (SDRAMP * 5), LASL), HSL}

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit |
| POWERTELEM | Gross or net real power provided via telemetry |
| SDRAMP | SCED down ramp rate |
| HSL | High Sustained Limit |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |