## Index
South to North Congestion
|  |  |  | AWGSF |  |  |  | Zone to Zone Transfers
Contingency | Overloaded element | OL Element flow direction | OL Kv | HOUSTON | NORTH | SOUTH | WEST | N to H | N to S | S to N | W to N | wksht
Sandow-Austrop | Butler-Elgin Switch | Butler to Elgin Switch | 138 | 0.0047639 | -0.0084979 | 0.015641 | -0.0077739 | -0.013262 | -0.024139 | 0.024139 | 0.00072394 | 1
Lyton Springs-Zorn Austrop-Zorn | Canyon-Rohr | Canyon to Rohr | 138 | 0.0015591 | -0.015272 | 0.030833 | -0.013038 | -0.016831 | -0.046104 | 0.046104 | 0.002234 | 2
Sandow-Austrop | Killeen Clark Road-Copperas Cove | Copperas Cove to Killeen Clark Road | 138 | 0.00040935 | -0.0075988 | 0.012348 | 0.00041543 | -0.0080082 | -0.019947 | 0.019947 | 0.0080143 | 3
Sandow-Temple | Killeen Clark Road-Copperas Cove | Copperas Cove to Killeen Clark Road | 138 | 0.0031681 | -0.016913 | 0.024288 | -0.0077905 | -0.020081 | -0.041201 | 0.041201 | 0.0091227 | 4
Sandow-Austrop | Sandow Transformer #1 | Low side to high side | 345/138 | -0.00095514 | -0.0099245 | 0.0022237 | -0.0092368 | -0.0089694 | -0.012148 | 0.012148 | 0.00068772 | 5
Lyton Springs-Zorn Austrop-Zorn | Zorn-Luling | Zorn to Luling | 138 | -0.00026474 | -0.0059971 | 0.014894 | -0.0041844 | -0.0057324 | -0.020891 | 0.020891 | 0.0018127 | 6

## Non move gen
BUS_NAM | BUS_NUM | Num
GIBCRK | 990 | 0
KINDERMG | 1069 | 0
KINDERMG | 1070 | 0
KINDERMG | 1071 | 0
BSP_1 | 1320 | 0
MOSES1 G | 1701 | 0
MOSES2 G | 1702 | 0
MOSES3 G | 1703 | 0
CMPK 1 G | 1898 | 0
CMPK 2 G | 1899 | 0
MTNLK 1G | 3097 | 0
MTNLK 2G | 3098 | 0
MTNLK 3G | 3099 | 0
BBRN 1 G | 3381 | 0
BBRN 2 G | 3382 | 0
SAND 4 G | 3432 | 0
JTD1 | 5111 | 0
JTD2 | 5112 | 0
JKS1 | 5401 | 0
SANMIGUE | 5903 | 0
STP1 | 5911 | 0
STP2 | 5912 | 0
WELSH 7 | 5920 | 0
NORTHDC7 | 6096 | 0
OKLAUN1G | 6752 | 0
FPP G1 | 7010 | 0
FPP G2 | 7011 | 0
FPP G3 | 7012 | 0
JOS #1 | 8139 | 0
CLO #1 | 8161 | 0
BAT #1 | 8388 | 0
BAT #2 | 8393 | 0
NBY #5 | 8437 | 0
NBY #6 | 8438 | 0
NBY #7 | 8442 | 0
TNPONE#1 | 39960 | 0
TNPONE#2 | 39970 | 0
LIM1 | 48721 | 0
LIM2 | 48722 | 0
PHR2 | 48772 | 0
WAP5 | 48925 | 0
WAP6 | 48926 | 0
WAP7 | 48927 | 0
WAP8 | 48928 | 0
DOW17000 | 49851 | 0
DOW38100 | 49858 | 0
DOW38200 | 49859 | 0
DOW38300 | 49860 | 0
DOW39100 | 49862 | 0
DOW39200 | 49863 | 0
DOW41000 | 49865 | 0
DOW42000 | 49866 | 0
DOW49000 | 49869 | 0
DOW61000 | 49870 | 0
DOW62000 | 49871 | 0
DOW63000 | 49872 | 0
DOW64000 | 49873 | 0
DOW65000 | 49876 | 0
DOW66000 | 49877 | 0
DOW67000 | 49878 | 0
DOW81000 | 49882 | 0
DOW82000 | 49884 | 0
DOW83000 | 49885 | 0
DOW84000 | 49886 | 0
REYSHR_G | 80223 | 0
VISTRONG | 80224 | 0
VISTRONG | 80225 | 0
ALCOA_G | 80226 | 0
AIRCO_G | 80227 | 0
CIDINDUS | 86105 | 0
SLURR | 88241 | 0

## 1
Generator Sensitivities
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
SANDOW_4G | -0.049 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 |  | 1.029 | 0 | 0 | 0 |  | Sum GSF*Pgen
LAKE_CRK2_G | -0.013 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -2.951 | 227 | HOUSTON | 65.863
THOUSE_2G | -0.013 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -10.465 | 805 | NORTH | -163.1671
THOUSE_1G | -0.013 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -7.319 | 563 | SOUTH | 217.26
LAKE_CRK1_G | -0.013 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -0.4602 | 35.4 | WEST | -38.317
BOSQUESW803 | -0.012 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -1.728 | 144
BOSQUESW804 | -0.012 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -0.996 | 83 |  | Sum Pgen
BOSQUESW502 | -0.012 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -1.788 | 149 | HOUSTON | 13825.3
BOSQUESW501 | -0.012 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -1.812 | 151 | NORTH | 19200.9
WHITNYDM01 | -0.011 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.165 | 15 | SOUTH | 13890.7
WHITNYDM02 | -0.011 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.165 | 15 | WEST | 4928.9
DECRDOVA_4G | -0.009 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.585 | 65
EAGLEMNT_3G | -0.009 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
JCKCNTY801 | -0.009 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -2.592 | 288 |  | AWGSF
MDLTHELP_2G | -0.009 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.935 | 215 | HOUSTON | 0.0047639
RWMILLER04 | -0.009 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -0.918 | 102 | NORTH | -0.0084979
HANDLEY_4G | -0.009 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -1.9575 | 217.5 | SOUTH | 0.015641
WLFHOLW_3G | -0.009 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -2.412 | 268 | WEST | -0.0077739
NTHTEXAS01 | -0.009 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.045 | 5
MDLTHELP_3G | -0.009 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.935 | 215
DECRDOVA_2G | -0.009 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -0.585 | 65 | N to H | -0.013262
JCKCNTY803 | -0.009 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -1.323 | 147 | N to S | -0.024139
WLFHOLW_1G | -0.009 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -1.944 | 216 | W to N | 0.00072394
RWMILLER05 | -0.009 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -0.909 | 101
HANDLEY_5G | -0.009 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
NTHTEXAS02 | -0.009 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.045 | 5
RWMILLER01 | -0.009 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -0.675 | 75
NTHTEXAS03 | -0.009 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.135 | 15
DECRDOVA_5G | -0.009 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.585 | 65
MDLTHELP_4G | -0.009 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -1.926 | 214
COMCHEPK_1G | -0.009 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
RWMILLER03 | -0.009 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -1.404 | 156
WLFHOLW_2G | -0.009 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -1.971 | 219
HANDLEY_1G | -0.009 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
ENNSTRAC_1G | -0.009 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -1.764 | 196
MDLTHELP_1G | -0.009 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.935 | 215
HANDLEY_3G | -0.009 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -3.1806 | 353.4
JNSNCNTY802 | -0.009 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -0.81 | 90
EAGLEMNT_1G | -0.009 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
JNSNCNTY802 | -0.009 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -1.512 | 168
RWMILLER02 | -0.009 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -1.071 | 119
JCKCNTY802 | -0.009 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -1.323 | 147
MDLTHELP_5G | -0.009 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -2.025 | 225
DECRDOVA_1G | -0.009 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -7.011 | 779
HANDLEY_2G | -0.009 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
COMCHEPK_2G | -0.009 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
DECRDOVA_3G | -0.009 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.585 | 65
MDLTHELP_6G | -0.009 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -2.061 | 229
ENNSTRAC_2G | -0.009 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -1.044 | 116
SLSTR1PP_1G | -0.009 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | -0.054 | 6
EAGLEMNT_2G | -0.009 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
LAMARPWR_2G | -0.008 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -1.24 | 155
OCOTILLO_1G | -0.008 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | -0.0464 | 5.8
OLINGER_G4 | -0.008 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.4728 | 59.1
MTCK8_G | -0.008 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -3.816 | 477
TGATEWAY_2G | -0.008 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -1.024 | 128
L_DIVIDE1_1N | -0.008 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | -0.212 | 26.5
BSP_1 | -0.008 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
HORSH1 | -0.008 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | -0.2664 | 33.3
PEC_1G | -0.008 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -0.64 | 80
CIELOGEN_2G | -0.008 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | -0.0488 | 6.1
MOSES_1G | -0.008 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
MRGNDG_4G | -0.008 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.56 | 70
FPLEFR2B_G | -0.008 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -1.28 | 160
L_GASCCR1_1N | -0.008 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | -0.12 | 15
TGATEWAY_4G | -0.008 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -3.192 | 399
SWETWATR_3G | -0.008 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | -0.544 | 68
MTCK3_G | -0.008 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
KINDERMG_1G | -0.008 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
CIRELLO | -0.008 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | -0.28 | 35
OLINGER_G3 | -0.008 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -0.9464 | 118.3
NTHLK3_G | -0.008 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -1.9792 | 247.4
SWETWATR_2G | -0.008 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | -0.576 | 72
DENISNDM | -0.008 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.32 | 40
SPENCER_G4 | -0.008 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.384 | 48
MRSSHPRD | -0.008 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.096 | 12
WFCOGEN_2G | -0.008 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.096 | 12
KINDERMG_2G | -0.008 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
AEPWIND_8 | -0.008 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | -0.1216 | 15.2
FPLEFR1B_G | -0.008 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -1.256 | 157
MRGNBG_2G | -0.008 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | -0.568 | 71
TRINIDAD_6G | -0.008 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -1.808 | 226
TIEHVCG_2G | -0.008 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.056 | 132
NAV6ST | -0.008 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.92 | 115
CALENG3G_3G | -0.008 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | -0.552 | 69
FPLEFR2C_G | -0.008 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -1.296 | 162
STRYKER_2G | -0.008 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -3.872 | 484
COLLIN_1G | -0.008 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
SWETWATR_1G | -0.008 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | -0.24 | 30
KMICHICT4_G | -0.008 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -1.088 | 136
HORSH2 | -0.008 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | -0.2208 | 27.6
NAV4CT | -0.008 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.64 | 80
NTHLK1_G | -0.008 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
CALENG1G_1G | -0.008 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | -0.584 | 73
CIELOGEN_1G | -0.008 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | -0.0792 | 9.9
MCDDONAL_8 | -0.008 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | -0.1712 | 21.4
BUFGGEN | -0.008 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | -0.144 | 18
ROSCOEW_5 | -0.008 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | -0.1672 | 20.9
MOSES_3G | -0.008 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0
NAV2CT | -0.008 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.64 | 80
NAV5CT | -0.008 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.64 | 80
MTCK2_G | -0.008 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
NAV1CT | -0.008 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.64 | 80
MARTLAKE_3G | -0.008 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
WCPWRCO_2G | -0.008 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -1.632 | 204
STEAM2 | -0.008 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.208 | 26
MESQUITW_2G | -0.008 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | -0.1888 | 23.6
OLINGER_G1 | -0.008 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -0.5048 | 63.1
KMICHICT2_G | -0.008 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -1.152 | 144
OKLAUN1G | -0.008 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
L_BITTCR1_1N | -0.008 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | -0.0448 | 5.6
FPLEFR2S_G | -0.008 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -3.296 | 412
STANTONW_8 | -0.008 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | -0.0808 | 10.1
STEAM3 | -0.008 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.328 | 41
MRGNAG_1G | -0.008 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | -0.552 | 69
GRHAMSES_1G | -0.008 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -1.936 | 242
WILDHRS11A | -0.008 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | -0.1008 | 12.6
LAMARPWR_5G | -0.008 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -1.304 | 163
L_SWEETW1_1N | -0.008 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | -0.1288 | 16.1
OLINGER_G2 | -0.008 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -0.6936 | 86.7
MRGNCG_3G | -0.008 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.56 | 70
LAMARPWR_4G | -0.008 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -1.312 | 164
MRSSHPRD01 | -0.008 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.096 | 12
MARTLAKE_2G | -0.008 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
MARTLAKE_1G | -0.008 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
LAMARPWR_3G | -0.008 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.592 | 199
HORSH4 | -0.008 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | -0.1376 | 17.2
MOSES_2G | -0.008 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
FPLEFR2A_G | -0.008 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.36 | 170
SNYDERW1A | -0.008 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | -0.0504 | 6.3
MRGNFG_6G | -0.008 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | -0.528 | 66
L_SWEETW1_3N | -0.008 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | -0.1424 | 17.8
HORSH3 | -0.008 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | -0.2688 | 33.6
PEC_3G | -0.008 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -0.728 | 91
KMICHICT5_G | -0.008 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -1.104 | 138
VALLLEY_1G | -0.008 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -1.12 | 140
DCEAST | -0.008 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -3.2024 | 400.3
KMICHICT1_G | -0.008 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -1.136 | 142
AIRTRICITY_8 | -0.008 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | -0.144 | 18
TIEHVSG_1G | -0.008 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.688 | 211
LAMARPWR_6G | -0.008 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.592 | 199
LONGSHORT_5 | -0.008 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | -0.12 | 15
VALLEY_2G | -0.008 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -4.216 | 527
FPLEFR1S_G | -0.008 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -3.312 | 414
L_SWEETW1_2N | -0.008 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | -0.1624 | 20.3
KINDERMG_3G | -0.008 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
TGATEWAY_3G | -0.008 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -1.168 | 146
KMICHIST6_G | -0.008 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -2.424 | 303
FPLEFR1A_G | -0.008 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.36 | 170
MORGAN5G_5G | -0.008 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | -1.096 | 137
SWETWATR_4G | -0.008 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | -0.488 | 61
TIEHVCG_4G | -0.008 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | -1.192 | 149
WFCOGEN_1G | -0.008 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.096 | 12
OKLA7A | -0.008 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.4 | 50
DANSBY2 | -0.008 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | -0.368 | 46
KMICHIST3_G | -0.008 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -2.48 | 310
LKHB2_G | -0.008 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -4.112 | 514
NTHLK2_G | -0.008 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
TIEHVCG_1G | -0.008 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | -1.16 | 145
SPENCER_G5 | -0.008 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.416 | 52
MRGNEG_5G | -0.008 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | -0.544 | 68
CHAMPION_1G | -0.008 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
CALHN_G1 | -0.008 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | -0.1368 | 17.1
TGATEWAY_1G | -0.008 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -1.192 | 149
SCURRYCW_1G | -0.008 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | -0.1128 | 14.1
TIEHVCG_3G | -0.008 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.056 | 132
LOUIS1A | -0.008 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | -0.204 | 25.5
NEWMAN_G5 | -0.008 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
MESQUITW_1G | -0.008 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | -0.32 | 40
ROSCOEWI_5 | -0.008 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | -0.1008 | 12.6
LKHB1_G | -0.008 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
FPLEFR1C_G | -0.008 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -1.272 | 159
RDCNYNG1 | -0.008 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | -0.0672 | 8.4
MTCK6_G | -0.008 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
LAMARPWR_1G | -0.008 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -1.232 | 154
MTCK7_G | -0.008 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
TRENTIPP_8 | -0.008 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | -0.18 | 22.5
GRHAMSES_2G | -0.008 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -2.952 | 369
WCPWRCO_3G | -0.008 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -1.936 | 242
WFCOGEN_1G | -0.008 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.096 | 12
DENISNDM | -0.008 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.32 | 40
TIEHVSG_2G | -0.008 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.688 | 211
NAV3ST | -0.008 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.92 | 115
VALLEY_3G | -0.008 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -1.4896 | 186.2
CALENG2G_2G | -0.008 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | -0.592 | 74
PEC_2G | -0.008 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -0.672 | 84
WCPWRCO_1G | -0.008 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -1.632 | 204
WHRLWIND1A | -0.008 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | -0.048 | 6
DANSBY14 | -0.008 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | -0.648 | 81
STRYKER_1G | -0.008 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -1.124 | 140.5
WFCOGEN_2G | -0.008 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.096 | 12
L_SWEETW1_4N | -0.008 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | -0.1256 | 15.7
STEAM1 | -0.008 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
BARTNWND_1G | -0.008 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.096 | 12
KM NWP | -0.007 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.084 | 12
RIO_DRCS | -0.007 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
CALFREST_4G | -0.007 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -1.092 | 156
ATKINS6 | -0.007 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0
PBCTCGE_3G | -0.007 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | -0.434 | 62
PBCTBGE_2G | -0.007 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | -0.455 | 65
NWPWRG1_1G | -0.007 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | -0.0238 | 3.4
WDWDU1 | -0.007 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | -0.084 | 12
KM SEP | -0.007 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | -0.042 | 6
ATKINS5 | -0.007 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0
BBRN_1G | -0.007 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
SWMESA | -0.007 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | -0.0784 | 11.2
TNWDWRDU2_8 | -0.007 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | -0.084 | 12
ATKINS4 | -0.007 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0
ATKINS7 | -0.007 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0
ATKINS3 | -0.007 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0
CALFREST_6G | -0.007 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -1.232 | 176
CALFREST_5G | -0.007 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -1.099 | 157
CALFREST_3G | -0.007 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -1.218 | 174
CALFREST_2G | -0.007 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -1.085 | 155
CALFREST_1G | -0.007 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -1.064 | 152
PB6GEN_7G | -0.007 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | -3.605 | 515
PB5GEN_6G | -0.007 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | -0.805 | 115
PBCTEGE_5G | -0.007 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | -0.455 | 65
PBCTDGE_4G | -0.007 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | -0.455 | 65
L_DELAWA1_1Y | -0.007 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | -0.0364 | 5.2
BBRN_2G | -0.007 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
L_DELAWA1_1Y | -0.007 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | -0.0315 | 4.5
WESTXWIN_1G | -0.007 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | -0.0049 | 0.7
KM SWP | -0.007 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.084 | 12
KM NEP | -0.007 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.084 | 12
PBCTAGE_1G | -0.007 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | -0.448 | 64
DSKY1 | -0.006 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | -0.0756 | 12.6
LEG_1___1 | -0.006 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
TAMUGEN1 | -0.006 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | -0.192 | 32
ORNNWP1 | -0.006 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | -0.072 | 12
DSKY2 | -0.006 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | -0.069 | 11.5
LEG_2___2 | -0.006 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
TNTNPONE_18 | -0.005 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
TNTNPONE_28 | -0.005 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
FRNDDRCS | -0.005 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
GIBN_CREK_G1 | -0.003 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
FTR_GT1_5105 | -0.002 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | -0.312 | 156
FTR_GT2_5110 | -0.002 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | -0.318 | 159
FTR_CN4_5095 | -0.002 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | -0.76 | 380
FTR_GT3_5085 | -0.002 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | -0.316 | 158
L_BUCHAN1_3Y | 0 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | 0 | 11
L_BUCHAN1_2Y | 0 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_1Y | 0 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | 0 | 14
L_INKSDA1_1Y | 0 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | 0 | 10
L_MARSFO1G2Y | 0.001 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | 0.016 | 16
L_MARSFO1G1Y | 0.001 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.022 | 22
L_MARSFO1G3Y | 0.001 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.022 | 22
L_MARBFA1_2Y | 0.002 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | 0.026 | 13
L_MARBFA1_1Y | 0.002 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_AUSTPL1_1Y | 0.002 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.014 | 7
L_FERGUS1_1Y | 0.002 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | 0.798 | 399
L_WIRTZ_1G2Y | 0.002 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | 0.036 | 18
L_AUSTPL1_1Y | 0.002 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.014 | 7
L_WIRTZ_1G1Y | 0.002 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
CVC_GT1_5035 | 0.003 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | 0.465 | 155
CVC_GT3_5045 | 0.003 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | 0.474 | 158
CVC_GT2_5020 | 0.003 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | 0.477 | 159
CVC_ST5_5040 | 0.003 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | 0.399 | 133
CHE_GT2_5030 | 0.003 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | 0.519 | 173
CAL_GT1_8045 | 0.004 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | 0.608 | 152
DPEC_GT15040 | 0.004 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | 0.648 | 162
LPE_GT4_8085 | 0.004 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.164 | 41
LPE_GT3_8080 | 0.004 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.164 | 41
LPE_GT1_8070 | 0.004 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.168 | 42
APD_GT1_8005 | 0.004 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | 0.56 | 140
DPEC_ST55065 | 0.004 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | 1.128 | 282
THW_5354 | 0.004 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0656 | 16.4
PSA_GT5_8140 | 0.004 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | 0.256 | 64
THW_4344 | 0.004 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.232 | 58
THW_5354 | 0.004 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0.0664 | 16.6
THW_5556 | 0.004 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0656 | 16.4
EXN941GT | 0.004 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.076 | 19
EXN_16GT | 0.004 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | 0.128 | 32
EXN_15GT | 0.004 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | 0.132 | 33
CBY_GN2_2 | 0.004 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | 3.004 | 751
EXN945GT | 0.004 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | 0.076 | 19
EP_1_2 | 0.004 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | 0.084 | 21
THW_4142 | 0.004 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.228 | 57
THW_5152 | 0.004 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0656 | 16.4
EXN_14GT | 0.004 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | 0.56 | 140
EXN_17GT | 0.004 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | 0.124 | 31
THW_5556 | 0.004 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0.0664 | 16.6
CBY_GN1_1 | 0.004 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | 2.992 | 748
BTE_GT3_8045 | 0.004 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | 0.632 | 158
EXN_GT | 0.004 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | 0.324 | 81
EXN944GT | 0.004 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | 0.132 | 33
EXN943GT | 0.004 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.076 | 19
EXN942GT | 0.004 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | 0.08 | 20
EXN938GT | 0.004 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | 0.172 | 43
SJS_GT1_GT1 | 0.004 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | 0.196 | 49
DPEC_GT35010 | 0.004 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | 0.64 | 160
LPE_GT2_8075 | 0.004 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.168 | 42
SRB_GN2_2 | 0.004 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | 0.696 | 174
THW_5152 | 0.004 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
GBY_GN5_5 | 0.004 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | 1.194 | 298.5
THW_GT1_GT_1 | 0.004 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
THW_4344 | 0.004 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.232 | 58
SRB_GT211035 | 0.004 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
PR_GT1__9040 | 0.004 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | 0.14 | 35
THW_3334 | 0.004 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.232 | 58
THW_3132 | 0.004 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.228 | 57
BTE_GT2_8075 | 0.004 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0.652 | 163
THW_ST4_ST_4 | 0.004 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | 0.432 | 108
THW_ST3_ST_3 | 0.004 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | 0.44 | 110
SRB_GT211035 | 0.004 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
SRB_GN4_4 | 0.004 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | 0.904 | 226
SRB_GN3_3 | 0.004 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | 0.88 | 220
SRB_GN1_1 | 0.004 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | 0.704 | 176
SOL_GT1 | 0.004 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | 0.0648 | 16.2
DIB_GT1_8080 | 0.004 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | 0.256 | 64
SJS_GT2_GT2 | 0.004 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | 0.196 | 49
SHELLG3_3020 | 0.004 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | 0.12 | 30
SHELLG3_3020 | 0.004 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | 0.156 | 39
SHELLG2 | 0.004 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | 0.288 | 72
SHELLG1_3015 | 0.004 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | 0.284 | 71
CVC_GT4_8005 | 0.004 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | 0.66 | 165
PSA_GT6_8135 | 0.004 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | 0.236 | 59
PSA_GN1_8165 | 0.004 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | 0.416 | 104
PSA_GT4_8145 | 0.004 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0.264 | 66
PSA_GT3_8150 | 0.004 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | 0.28 | 70
PSA_GT2_8155 | 0.004 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0.264 | 66
PSA_GT1_8160 | 0.004 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | 0.26 | 65
PSG_GT3_8060 | 0.004 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.656 | 164
PSG_GT2_8040 | 0.004 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.656 | 164
PSG_GN2_8050 | 0.004 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | 0.712 | 178
EP_1_2 | 0.004 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | 0.02 | 5
THW_4142 | 0.004 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.232 | 58
DPEC_GT45070 | 0.004 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | 0.632 | 158
DPEC_GT25025 | 0.004 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | 0.624 | 156
THW_3334 | 0.004 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.232 | 58
DIB_GT3_8090 | 0.004 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | 0.3088 | 77.2
DIB_ST1_8085 | 0.004 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | 0.276 | 69
DIB_GT2_8075 | 0.004 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.26 | 65
BTE_ST1_8070 | 0.004 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | 0.936 | 234
BTE_GT4_8055 | 0.004 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0.652 | 163
THW_3132 | 0.004 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.228 | 57
CHE_GN4_8025 | 0.004 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | 0.568 | 142
CHE_GT1_8015 | 0.004 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | 0.692 | 173
CAL_ST1_8000 | 0.004 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.26 | 65
PHR_GN2_2 | 0.005 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
GBY_83841065 | 0.005 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | 0.1 | 20
GBY_83841065 | 0.005 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | 0.1 | 20
GBY_81821075 | 0.005 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.24 | 48
GBY_73741085 | 0.005 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | 0.235 | 47
GBY_73741085 | 0.005 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.24 | 48
CTL_GN1_8145 | 0.005 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | 0.275 | 55
CTL_GT4_8140 | 0.005 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | 0.47 | 94
CTL_GT3_8135 | 0.005 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | 0.455 | 91
BYU_GT4_8065 | 0.005 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.325 | 65
BYU_GT3_8060 | 0.005 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | 0.335 | 67
BYU_GT2_8055 | 0.005 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | 0.31 | 62
BYU_GT1_8075 | 0.005 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.325 | 65
TNDOWCGNGG8 | 0.005 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | 0.15 | 30
TNDOWCGNSG8 | 0.005 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | 0.16 | 32
TNSLCGN1__8 | 0.005 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | 0.15 | 30
TNTXCTY3CG8 | 0.005 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | 0.425 | 85
TNTXCTY2CG8 | 0.005 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | 0.51 | 102
TNTXCTY1CG8 | 0.005 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | 0.525 | 105
TNBPAMCG4_8 | 0.005 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | 0.48 | 96
TNBPAMCG3_8 | 0.005 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | 0.76 | 152
TNBPAMCG2_8 | 0.005 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | 0.75 | 150
TNBP_CGN3_8 | 0.005 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | 0.265 | 53
TNBP_CGN2_8 | 0.005 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | 0.33 | 66
TNBP_CGN1_8 | 0.005 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | 0.3 | 60
CTL_GT2_8130 | 0.005 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | 0.515 | 103
TNBPAMCG1_8 | 0.005 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | 0.775 | 155
TNBP_CGN4_8 | 0.005 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | 0.2 | 40
TNTXCTY4CG8 | 0.005 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | 0.515 | 103
CTL_GN2_8155 | 0.005 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | 0.055 | 11
GBY_81821075 | 0.005 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | 0.1 | 20
AMISTADHDRO2 | 0.006 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | 0.078 | 13
AMISTADHDRO1 | 0.006 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | 0.099 | 16.5
WAP_GN8_8 | 0.006 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
WAP_GN7_7 | 0.006 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN4_4 | 0.006 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | 3.264 | 544
DECKR_G1 | 0.006 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | 1.92 | 320
WAP_GN3_3 | 0.006 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | 1.356 | 226
WAP_GN1_1 | 0.006 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | 0.747 | 124.5
BVE_ST1_GN1 | 0.006 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | 1.476 | 246
BVE_GT2_5035 | 0.006 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | 1.02 | 170
BVE_GT1_GT1 | 0.006 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | 1.032 | 172
WAP_GN6_6 | 0.006 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
WAP_GN2_2 | 0.006 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | 0.7332 | 122.2
SANDHG5C | 0.006 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | 0.84 | 140
SANDH_G4 | 0.006 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.27 | 45
SANDH_G3 | 0.006 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | 0.27 | 45
SANDH_G2 | 0.006 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.27 | 45
DECKR_G2 | 0.006 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | 2.4 | 400
WAPGT21_GT1 | 0.006 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
MNS_GT | 0.006 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | 0.2766 | 46.1
WAP_GN5_5 | 0.006 | 48925 | 5 | HOUSTON | YES | 216.7 | 278 | 657 | 0 | 1 | 0 | 0 | 0
HAMILTON | 0.006 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
SANDH_G1 | 0.006 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | 0.27 | 45
SANDHG5A | 0.006 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | 0.9 | 150
AK_GT1__8040 | 0.006 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | 0.204 | 34
DOW62000 | 0.007 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
DOW49000 | 0.007 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
DOW41000 | 0.007 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW66000 | 0.007 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
DOW38300 | 0.007 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
BSF_GT1_8070 | 0.007 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | 0.07 | 10
TNSCLP2___8 | 0.007 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | 0.819 | 117
DOW64000 | 0.007 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
DOW65000 | 0.007 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
DOW81000 | 0.007 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
DOW63000 | 0.007 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
BSF_GT1_8070 | 0.007 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | 0.504 | 72
DOW83000 | 0.007 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW84000 | 0.007 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
DOW82000 | 0.007 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
TNSCLP3___8 | 0.007 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | 0.777 | 111
DOW61000 | 0.007 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
DOW39200 | 0.007 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
TNSCLP1___8 | 0.007 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | 0.812 | 116
TNSCLP4___8 | 0.007 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | 0.805 | 115
DOW67000 | 0.007 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW17000 | 0.007 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
DOW38200 | 0.007 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW38100 | 0.007 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
DOW39100 | 0.007 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
DOW42000 | 0.007 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
STP_GN2___2 | 0.008 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
STP_GN1___1 | 0.008 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
EPLVT1 | 0.008 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
ELPS | 0.008 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | 0.048 | 6
TGF_GT1_8000 | 0.01 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | 0.692 | 69.2
L_BASTEN1_3Y | 0.01 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | 2.27 | 227
L_BASTEN1_2Y | 0.01 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | 1.46 | 146
DECKR_G4 | 0.01 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.44 | 44
DECKR_G6 | 0.01 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | 0.44 | 44
L_BASTEN1_1Y | 0.01 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | 1.47 | 147
DECKR_G3 | 0.01 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0
DECKR_G5 | 0.01 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.44 | 44
CBE_GT1 | 0.011 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.946 | 86
PEARSALLGEN3 | 0.011 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | 0.0682 | 6.2
CBE_ST12 | 0.011 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 1.1385 | 103.5
LAR_3 | 0.011 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | 0.8668 | 78.8
PEARSALLGEN2 | 0.011 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.0682 | 6.2
CBE_GT3 | 0.011 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.946 | 86
LAR_1 | 0.011 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | 0.176 | 16
LAR | 0.011 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
CBE_ST34 | 0.011 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 1.1385 | 103.5
CIDINDUS | 0.011 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
PEARSALLGEN1 | 0.011 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.0682 | 6.2
CBE_GT2 | 0.011 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.946 | 86
CBE_GT4 | 0.011 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.946 | 86
LAR_2 | 0.011 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | 0.099 | 9
HECN1 | 0.012 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 1.776 | 148
SANMIGUELGEN | 0.012 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
SI_RAY9 | 0.012 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 0.456 | 38
OWS1 | 0.012 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | 5.004 | 417
SI_RAY5 | 0.012 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0.12 | 10
COSW_1 | 0.012 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0.24 | 20
L_GUADGE1_3Y | 0.012 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | 1.752 | 146
CNOPST1 | 0.012 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.836 | 153
WBT1 | 0.012 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | 0.306 | 25.5
HECN2 | 0.012 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 1.776 | 148
LCP3 | 0.012 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | 0.696 | 58
SI_RAY10 | 0.012 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 0.564 | 47
FALCONHYDRO3 | 0.012 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | 0.0336 | 2.8
WBT2 | 0.012 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | 0.96 | 80
AVR1_CT1 | 0.012 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | 1.8 | 150
OWS2 | 0.012 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | 4.548 | 379
STARCO_1 | 0.012 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 0.456 | 38
L_LOSTPI1_3Y | 0.012 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | 2.0868 | 173.9
LCPCT4 | 0.012 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 0.54 | 45
VHB1 | 0.012 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | 2.472 | 206
COSW_2 | 0.012 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0.168 | 14
JTD2 | 0.012 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
ICPGN#1 | 0.012 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 1.788 | 149
L_RIONOG1G2Y | 0.012 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | 1.776 | 148
HECN3 | 0.012 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 2.028 | 169
MVGN#2 | 0.012 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 2.46 | 205
WBT3 | 0.012 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | 1.152 | 96
ICPGN#3 | 0.012 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 1.524 | 127
ZAPATA | 0.012 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
LCPCT2 | 0.012 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | 0.552 | 46
FGNTS201 | 0.012 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 2.064 | 172
MILHWYS | 0.012 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
LGEGN#3 | 0.012 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 1.092 | 91
ICPGN#2 | 0.012 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 1.8 | 150
VHB2 | 0.012 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | 2.64 | 220
REYSHR_G | 0.012 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
FALCONHYDRO2 | 0.012 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.036 | 3
JTD1 | 0.012 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
L_HAYSEN1_4Y | 0.012 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | 2.748 | 229
LGEGN#1 | 0.012 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 1.896 | 158
LCPCT1 | 0.012 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 0.54 | 45
FALCONHYDRO1 | 0.012 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.036 | 3
MVGN#3 | 0.012 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 3.084 | 257
CNOPGT1 | 0.012 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 1.968 | 164
WBT4 | 0.012 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | 1.812 | 151
CNOPGT2 | 0.012 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 1.98 | 165
VHB3 | 0.012 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | 4.764 | 397
FGNTS001 | 0.012 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 1.704 | 142
LCPCT3 | 0.012 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | 0.528 | 44
VAL_2 | 0.012 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.3 | 25
AVR1_ST1 | 0.012 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | 1.968 | 164
VAL_1 | 0.012 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.3 | 25
CEL_B_1 | 0.012 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 0.348 | 29
L_GUADGE1_4Y | 0.012 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | 1.788 | 149
SI_RAY6 | 0.012 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0.228 | 19
L_GUADGE1_1Y | 0.012 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | 1.812 | 151
L_GUADGE1_6Y | 0.012 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | 2.448 | 204
JKS1 | 0.012 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
L_LOSTPI1_2Y | 0.012 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | 1.8924 | 157.7
L_HAYSEN1_1Y | 0.012 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | 2.676 | 223
DAV_2 | 0.012 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 4.08 | 340
FALFURRI | 0.012 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
L_LOSTPI1_1Y | 0.012 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | 1.9044 | 158.7
L_GUADGE1_5Y | 0.012 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | 2.196 | 183
L_HAYSEN1_3Y | 0.012 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | 2.712 | 226
L_GUADGE1_2Y | 0.012 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | 1.668 | 139
AVR1_CT2 | 0.012 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | 1.74 | 145
SLURR | 0.012 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
L_RIONOG1G3Y | 0.012 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | 1.8 | 150
L_RIONOG1S1Y | 0.012 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | 3.516 | 293
LGEGN#2 | 0.012 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.836 | 153
MVGN#1 | 0.012 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 2.52 | 210
LCP4 | 0.012 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | 1.14 | 95
FGNTS101 | 0.012 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 1.752 | 146
KOCHREF2 | 0.012 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 0.456 | 38
L_RIONOG1G1Y | 0.012 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | 1.764 | 147
DAV_1 | 0.012 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 4.068 | 339
L_HAYSEN1_2Y | 0.012 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | 2.688 | 224
CLO_1 | 0.013 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
RAYBURNCC7 | 0.014 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 0.686 | 49
CSDR89 | 0.014 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.546 | 39
RAYBURNCC9 | 0.014 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.7 | 50
FOR_4 | 0.014 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | 1.0444 | 74.6
FOR_6 | 0.014 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | 0.364 | 26
RAYBURNGEN2 | 0.014 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
VISTRONG2 | 0.014 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
FOR_1 | 0.014 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | 0.7896 | 56.4
FOR_2 | 0.014 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | 0.9212 | 65.8
CSDR56 | 0.014 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.21 | 15
FOR_3 | 0.014 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | 0.9212 | 65.8
FOR_9 | 0.014 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | 0.448 | 32
UCAR_2 | 0.014 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | 0.294 | 21
AIRCO_G | 0.014 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
CSDR7 | 0.014 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | 0.098 | 7
ALCOA_G | 0.014 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
VISTRONG1 | 0.014 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
CSDR56 | 0.014 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.546 | 39
RAYBURNGEN1 | 0.014 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
CSDR89 | 0.014 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.21 | 15
RAYBURNGEN3 | 0.014 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0.0868 | 6.2
FOR_8 | 0.014 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | 0.392 | 28
CSDR11 | 0.014 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | 0.546 | 39
L_SCHUMA8_1Y | 0.014 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
BEEVILLE | 0.014 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
UCAR_1 | 0.014 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | 0.098 | 7
RAYBURNCC8 | 0.014 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.7 | 50
RAYBURNCC10 | 0.014 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 0.56 | 40
FOR_5 | 0.014 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | 0.945 | 67.5
FOR_10 | 0.014 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | 1.022 | 73
FOR_7 | 0.014 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | 0.644 | 46
DUP1V_1 | 0.015 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | 1.095 | 73
L_CANYHY8_1Y | 0.016 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.018 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.018 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_FPPYD11_2Y | 0.018 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_1Y | 0.018 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0
L_MCQUEE9_1Y | 0.018 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
L_FPPYD21_3Y | 0.018 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
CUECPL2A | 0.027 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | 0.324 | 12
L_LAKEWO9_1Y | 0.028 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_LAKEWO9_1Y | 0.028 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_SIMGID1_3Y | 0.118 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | 38.3382 | 324.9
L_SIMGID1_1Y | 0.118 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | 15.694 | 133
L_SIMGID1_2Y | 0.118 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | 15.694 | 133

## 2
Generator Sensitivities
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
L_AUSTPL1_1Y | -0.057 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | -0.399 | 7 |  | Sum GSF*Pgen
L_AUSTPL1_1Y | -0.057 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | -0.399 | 7 | HOUSTON | 21.555
SANDH_G2 | -0.055 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | -2.475 | 45 | NORTH | -293.2284
SANDH_G1 | -0.055 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | -2.475 | 45 | SOUTH | 428.2892
SANDHG5C | -0.055 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | -7.7 | 140 | WEST | -64.2612
SANDH_G4 | -0.055 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | -2.475 | 45
SANDH_G3 | -0.055 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | -2.475 | 45 |  | Sum Pgen
SANDHG5A | -0.055 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | -8.25 | 150 | HOUSTON | 13825.3
DECKR_G1 | -0.053 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | -16.96 | 320 | NORTH | 19200.9
DECKR_G2 | -0.053 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | -21.2 | 400 | SOUTH | 13890.7
L_MARSFO1G1Y | -0.049 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | -1.078 | 22 | WEST | 4928.9
L_MARSFO1G3Y | -0.049 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | -1.078 | 22
L_MARSFO1G2Y | -0.049 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | -0.784 | 16
DECKR_G5 | -0.048 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | -2.112 | 44 |  | AWGSF
DECKR_G4 | -0.048 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | -2.112 | 44 | HOUSTON | 0.0015591
DECKR_G6 | -0.048 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | -2.112 | 44 | NORTH | -0.015272
DECKR_G3 | -0.048 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0 | SOUTH | 0.030833
L_SIMGID1_3Y | -0.045 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | -14.6205 | 324.9 | WEST | -0.013038
L_SIMGID1_2Y | -0.045 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | -5.985 | 133
L_SIMGID1_1Y | -0.045 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | -5.985 | 133
L_BASTEN1_3Y | -0.04 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | -9.08 | 227 | N to H | -0.016831
L_BASTEN1_1Y | -0.04 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | -5.88 | 147 | N to S | -0.046104
L_BASTEN1_2Y | -0.04 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | -5.84 | 146 | W to N | 0.002234
L_LOSTPI1_1Y | -0.036 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | -5.7132 | 158.7
L_LOSTPI1_2Y | -0.036 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | -5.6772 | 157.7
L_LOSTPI1_3Y | -0.036 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | -6.2604 | 173.9
SANDOW_4G | -0.034 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 | 0 | 1.029 | 0 | 0 | 0
L_MARBFA1_2Y | -0.032 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | -0.416 | 13
L_MARBFA1_1Y | -0.032 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_FPPYD21_3Y | -0.031 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_1Y | -0.031 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_2Y | -0.031 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0
L_BUCHAN1_1Y | -0.03 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | -0.42 | 14
L_BUCHAN1_2Y | -0.03 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_3Y | -0.03 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | -0.33 | 11
L_WIRTZ_1G1Y | -0.027 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
L_WIRTZ_1G2Y | -0.027 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | -0.486 | 18
L_INKSDA1_1Y | -0.026 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | -0.26 | 10
L_FERGUS1_1Y | -0.024 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | -9.576 | 399
LAKE_CRK2_G | -0.021 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -4.767 | 227
THOUSE_1G | -0.021 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -11.823 | 563
BOSQUESW502 | -0.021 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -3.129 | 149
BOSQUESW501 | -0.021 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -3.171 | 151
THOUSE_2G | -0.021 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -16.905 | 805
LAKE_CRK1_G | -0.021 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -0.7434 | 35.4
BOSQUESW803 | -0.02 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -2.88 | 144
BOSQUESW804 | -0.02 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -1.66 | 83
WHITNYDM02 | -0.019 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.285 | 15
WHITNYDM01 | -0.019 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.285 | 15
MDLTHELP_6G | -0.016 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -3.664 | 229
MDLTHELP_4G | -0.016 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -3.424 | 214
SLSTR1PP_1G | -0.016 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | -0.096 | 6
MDLTHELP_5G | -0.016 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -3.6 | 225
DECRDOVA_3G | -0.016 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -1.04 | 65
DECRDOVA_5G | -0.016 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -1.04 | 65
DECRDOVA_1G | -0.016 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -12.464 | 779
JNSNCNTY802 | -0.016 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -2.688 | 168
RWMILLER03 | -0.016 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -2.496 | 156
RWMILLER04 | -0.016 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -1.632 | 102
JNSNCNTY802 | -0.016 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -1.44 | 90
MDLTHELP_1G | -0.016 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.44 | 215
RWMILLER02 | -0.016 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -1.904 | 119
DECRDOVA_4G | -0.016 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -1.04 | 65
RWMILLER01 | -0.016 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -1.2 | 75
RWMILLER05 | -0.016 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -1.616 | 101
MDLTHELP_3G | -0.016 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.44 | 215
DECRDOVA_2G | -0.016 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -1.04 | 65
MDLTHELP_2G | -0.016 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.44 | 215
TRINIDAD_6G | -0.015 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -3.39 | 226
MRSSHPRD01 | -0.015 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.18 | 12
WCPWRCO_3G | -0.015 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -3.63 | 242
HANDLEY_2G | -0.015 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
VALLLEY_1G | -0.015 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -2.1 | 140
MARTLAKE_1G | -0.015 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
KMICHIST3_G | -0.015 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -4.65 | 310
STEAM1 | -0.015 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
KMICHICT5_G | -0.015 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -2.07 | 138
FPLEFR1C_G | -0.015 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -2.385 | 159
BARTNWND_1G | -0.015 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.18 | 12
KMICHICT1_G | -0.015 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -2.13 | 142
MTCK7_G | -0.015 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
WLFHOLW_2G | -0.015 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -3.285 | 219
MARTLAKE_3G | -0.015 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
NTHTEXAS01 | -0.015 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.075 | 5
WLFHOLW_3G | -0.015 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -4.02 | 268
MTCK6_G | -0.015 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
MRSSHPRD | -0.015 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.18 | 12
EAGLEMNT_2G | -0.015 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
PEC_2G | -0.015 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -1.26 | 84
VALLEY_2G | -0.015 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -7.905 | 527
MOSES_3G | -0.015 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0
EAGLEMNT_1G | -0.015 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
WLFHOLW_1G | -0.015 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -3.24 | 216
OLINGER_G4 | -0.015 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.8865 | 59.1
NEWMAN_G5 | -0.015 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
EAGLEMNT_3G | -0.015 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
LAMARPWR_3G | -0.015 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -2.985 | 199
LAMARPWR_4G | -0.015 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -2.46 | 164
LAMARPWR_1G | -0.015 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -2.31 | 154
PEC_3G | -0.015 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -1.365 | 91
MOSES_2G | -0.015 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
MTCK2_G | -0.015 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
DENISNDM | -0.015 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.6 | 40
MTCK8_G | -0.015 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -7.155 | 477
WCPWRCO_1G | -0.015 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -3.06 | 204
STEAM2 | -0.015 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.39 | 26
NTHTEXAS03 | -0.015 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.225 | 15
HANDLEY_1G | -0.015 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
PEC_1G | -0.015 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -1.2 | 80
SPENCER_G4 | -0.015 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.72 | 48
OLINGER_G2 | -0.015 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -1.3005 | 86.7
OLINGER_G1 | -0.015 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -0.9465 | 63.1
FPLEFR2C_G | -0.015 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -2.43 | 162
FPLEFR1S_G | -0.015 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -6.21 | 414
FPLEFR1A_G | -0.015 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -2.55 | 170
KMICHIST6_G | -0.015 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -4.545 | 303
KMICHICT4_G | -0.015 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -2.04 | 136
KMICHICT2_G | -0.015 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -2.16 | 144
MARTLAKE_2G | -0.015 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
NTHLK2_G | -0.015 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
COMCHEPK_1G | -0.015 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
LAMARPWR_6G | -0.015 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -2.985 | 199
WFCOGEN_2G | -0.015 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.18 | 12
WCPWRCO_2G | -0.015 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -3.06 | 204
COMCHEPK_2G | -0.015 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
MTCK3_G | -0.015 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
WFCOGEN_2G | -0.015 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.18 | 12
FPLEFR1B_G | -0.015 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -2.355 | 157
JCKCNTY802 | -0.015 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -2.205 | 147
WFCOGEN_1G | -0.015 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.18 | 12
LKHB2_G | -0.015 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -7.71 | 514
WFCOGEN_1G | -0.015 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.18 | 12
JCKCNTY803 | -0.015 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -2.205 | 147
FPLEFR2S_G | -0.015 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -6.18 | 412
HANDLEY_3G | -0.015 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -5.301 | 353.4
GRHAMSES_1G | -0.015 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -3.63 | 242
NTHLK3_G | -0.015 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -3.711 | 247.4
FPLEFR2B_G | -0.015 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -2.4 | 160
LAMARPWR_2G | -0.015 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -2.325 | 155
DENISNDM | -0.015 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.6 | 40
ENNSTRAC_2G | -0.015 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -1.74 | 116
STEAM3 | -0.015 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.615 | 41
GRHAMSES_2G | -0.015 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -5.535 | 369
NTHTEXAS02 | -0.015 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.075 | 5
HANDLEY_4G | -0.015 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -3.2625 | 217.5
LAMARPWR_5G | -0.015 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -2.445 | 163
VALLEY_3G | -0.015 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -2.793 | 186.2
HANDLEY_5G | -0.015 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
ENNSTRAC_1G | -0.015 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -2.94 | 196
JCKCNTY801 | -0.015 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -4.32 | 288
MOSES_1G | -0.015 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
OLINGER_G3 | -0.015 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -1.7745 | 118.3
LKHB1_G | -0.015 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
DCEAST | -0.015 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -6.0045 | 400.3
NTHLK1_G | -0.015 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
SPENCER_G5 | -0.015 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.78 | 52
COLLIN_1G | -0.015 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
FPLEFR2A_G | -0.015 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -2.55 | 170
STRYKER_2G | -0.014 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -6.776 | 484
CALFREST_3G | -0.014 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -2.436 | 174
CALFREST_5G | -0.014 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -2.198 | 157
CALFREST_1G | -0.014 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -2.128 | 152
WILDHRS11A | -0.014 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | -0.1764 | 12.6
BBRN_1G | -0.014 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
OKLA7A | -0.014 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.7 | 50
OKLAUN1G | -0.014 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
CALFREST_6G | -0.014 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -2.464 | 176
CALFREST_4G | -0.014 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -2.184 | 156
CALFREST_2G | -0.014 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -2.17 | 155
TGATEWAY_4G | -0.014 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -5.586 | 399
TGATEWAY_3G | -0.014 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -2.044 | 146
TGATEWAY_2G | -0.014 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -1.792 | 128
TGATEWAY_1G | -0.014 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -2.086 | 149
STRYKER_1G | -0.014 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -1.967 | 140.5
MESQUITW_2G | -0.014 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | -0.3304 | 23.6
MESQUITW_1G | -0.014 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | -0.56 | 40
WHRLWIND1A | -0.014 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | -0.084 | 6
BBRN_2G | -0.014 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
CHAMPION_1G | -0.014 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
KINDERMG_2G | -0.013 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
TIEHVCG_2G | -0.013 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.716 | 132
SWETWATR_2G | -0.013 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | -0.936 | 72
TIEHVSG_2G | -0.013 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -2.743 | 211
NAV5CT | -0.013 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -1.04 | 80
KINDERMG_1G | -0.013 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
SCURRYCW_1G | -0.013 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | -0.1833 | 14.1
CIELOGEN_2G | -0.013 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | -0.0793 | 6.1
SWETWATR_4G | -0.013 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | -0.793 | 61
CIELOGEN_1G | -0.013 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | -0.1287 | 9.9
LONGSHORT_5 | -0.013 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | -0.195 | 15
RDCNYNG1 | -0.013 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | -0.1092 | 8.4
HORSH3 | -0.013 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | -0.4368 | 33.6
CALENG3G_3G | -0.013 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | -0.897 | 69
SNYDERW1A | -0.013 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | -0.0819 | 6.3
CALENG2G_2G | -0.013 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | -0.962 | 74
MCDDONAL_8 | -0.013 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | -0.2782 | 21.4
CALENG1G_1G | -0.013 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | -0.949 | 73
MRGNFG_6G | -0.013 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | -0.858 | 66
ROSCOEWI_5 | -0.013 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | -0.1638 | 12.6
TRENTIPP_8 | -0.013 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | -0.2925 | 22.5
CIRELLO | -0.013 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | -0.455 | 35
MRGNEG_5G | -0.013 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | -0.884 | 68
LOUIS1A | -0.013 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | -0.3315 | 25.5
MRGNDG_4G | -0.013 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.91 | 70
ROSCOEW_5 | -0.013 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | -0.2717 | 20.9
CALHN_G1 | -0.013 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | -0.2223 | 17.1
HORSH1 | -0.013 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | -0.4329 | 33.3
MRGNCG_3G | -0.013 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.91 | 70
BSP_1 | -0.013 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
MRGNBG_2G | -0.013 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | -0.923 | 71
MRGNAG_1G | -0.013 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | -0.897 | 69
MORGAN5G_5G | -0.013 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | -1.781 | 137
L_SWEETW1_3N | -0.013 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | -0.2314 | 17.8
L_SWEETW1_1N | -0.013 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | -0.2093 | 16.1
L_BITTCR1_1N | -0.013 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | -0.0728 | 5.6
L_SWEETW1_4N | -0.013 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | -0.2041 | 15.7
TIEHVCG_4G | -0.013 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | -1.937 | 149
TIEHVCG_3G | -0.013 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.716 | 132
TIEHVCG_1G | -0.013 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | -1.885 | 145
TIEHVSG_1G | -0.013 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -2.743 | 211
NAV6ST | -0.013 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -1.495 | 115
NAV4CT | -0.013 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -1.04 | 80
NAV3ST | -0.013 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -1.495 | 115
NAV2CT | -0.013 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -1.04 | 80
L_GASCCR1_1N | -0.013 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | -0.195 | 15
NAV1CT | -0.013 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -1.04 | 80
SWETWATR_1G | -0.013 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | -0.39 | 30
HORSH4 | -0.013 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | -0.2236 | 17.2
SWETWATR_3G | -0.013 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | -0.884 | 68
STANTONW_8 | -0.013 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | -0.1313 | 10.1
AIRTRICITY_8 | -0.013 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | -0.234 | 18
L_SWEETW1_2N | -0.013 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | -0.2639 | 20.3
OCOTILLO_1G | -0.013 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | -0.0754 | 5.8
AEPWIND_8 | -0.013 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | -0.1976 | 15.2
HORSH2 | -0.013 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | -0.3588 | 27.6
WESTXWIN_1G | -0.013 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | -0.0091 | 0.7
BUFGGEN | -0.013 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | -0.234 | 18
NWPWRG1_1G | -0.013 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | -0.0442 | 3.4
L_DIVIDE1_1N | -0.013 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | -0.3445 | 26.5
KINDERMG_3G | -0.013 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
L_DELAWA1_1Y | -0.012 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | -0.0624 | 5.2
L_DELAWA1_1Y | -0.012 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | -0.054 | 4.5
LEG_2___2 | -0.012 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
LEG_1___1 | -0.012 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
PB6GEN_7G | -0.012 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | -6.18 | 515
PB5GEN_6G | -0.012 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | -1.38 | 115
PBCTEGE_5G | -0.012 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | -0.78 | 65
PBCTDGE_4G | -0.012 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | -0.78 | 65
PBCTCGE_3G | -0.012 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | -0.744 | 62
PBCTBGE_2G | -0.012 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | -0.78 | 65
PBCTAGE_1G | -0.012 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | -0.768 | 64
TNTNPONE_28 | -0.011 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
TNTNPONE_18 | -0.011 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
DANSBY14 | -0.011 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | -0.891 | 81
DANSBY2 | -0.011 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | -0.506 | 46
ATKINS5 | -0.01 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0
SWMESA | -0.01 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | -0.112 | 11.2
TNWDWRDU2_8 | -0.01 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | -0.12 | 12
ATKINS4 | -0.01 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0
ATKINS7 | -0.01 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0
ATKINS6 | -0.01 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0
ATKINS3 | -0.01 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0
TAMUGEN1 | -0.01 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | -0.32 | 32
RIO_DRCS | -0.01 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
KM NEP | -0.01 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.12 | 12
WDWDU1 | -0.01 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | -0.12 | 12
KM SWP | -0.01 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.12 | 12
KM NWP | -0.01 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.12 | 12
KM SEP | -0.01 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | -0.06 | 6
DSKY1 | -0.009 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | -0.1134 | 12.6
ORNNWP1 | -0.009 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | -0.108 | 12
DSKY2 | -0.009 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | -0.1035 | 11.5
GIBN_CREK_G1 | -0.007 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
FTR_CN4_5095 | -0.006 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | -2.28 | 380
FTR_GT3_5085 | -0.006 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | -0.948 | 158
FTR_GT1_5105 | -0.006 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | -0.936 | 156
FTR_GT2_5110 | -0.006 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | -0.954 | 159
FRNDDRCS | -0.005 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
CVC_GT2_5020 | -0.001 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | -0.159 | 159
CVC_ST5_5040 | -0.001 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | -0.133 | 133
CVC_GT1_5035 | -0.001 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | -0.155 | 155
CVC_GT3_5045 | -0.001 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | -0.158 | 158
CHE_GT2_5030 | -0.001 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | -0.173 | 173
THW_5556 | 0 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
THW_5354 | 0 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0 | 16.6
THW_5354 | 0 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
THW_5152 | 0 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
THW_GT1_GT_1 | 0 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
CVC_GT4_8005 | 0 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | 0 | 165
PSA_GT6_8135 | 0 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | 0 | 59
PSA_GN1_8165 | 0 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | 0 | 104
PSA_GT4_8145 | 0 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0 | 66
PSA_GT3_8150 | 0 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | 0 | 70
PSA_GT2_8155 | 0 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0 | 66
PSA_GT1_8160 | 0 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | 0 | 65
GBY_GN5_5 | 0 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | 0 | 298.5
BTE_ST1_8070 | 0 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | 0 | 234
BTE_GT4_8055 | 0 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0 | 163
BTE_GT3_8045 | 0 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | 0 | 158
THW_5556 | 0 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0 | 16.6
BTE_GT2_8075 | 0 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0 | 163
THW_5152 | 0 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
PSA_GT5_8140 | 0 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | 0 | 64
EXN_GT | 0.001 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | 0.081 | 81
SRB_GN2_2 | 0.001 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | 0.174 | 174
EXN944GT | 0.001 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | 0.033 | 33
EXN942GT | 0.001 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | 0.02 | 20
THW_4142 | 0.001 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.057 | 57
EXN938GT | 0.001 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | 0.043 | 43
EXN_17GT | 0.001 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | 0.031 | 31
EXN_16GT | 0.001 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | 0.032 | 32
THW_4344 | 0.001 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.058 | 58
SRB_GT211035 | 0.001 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
THW_4142 | 0.001 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.058 | 58
THW_3334 | 0.001 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.058 | 58
THW_3334 | 0.001 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.058 | 58
THW_3132 | 0.001 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.057 | 57
THW_ST4_ST_4 | 0.001 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | 0.108 | 108
THW_ST3_ST_3 | 0.001 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | 0.11 | 110
SRB_GT211035 | 0.001 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
SRB_GN3_3 | 0.001 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | 0.22 | 220
THW_4344 | 0.001 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.058 | 58
SRB_GN1_1 | 0.001 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | 0.176 | 176
SOL_GT1 | 0.001 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | 0.0162 | 16.2
SJS_GT2_GT2 | 0.001 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | 0.049 | 49
SRB_GN4_4 | 0.001 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | 0.226 | 226
SJS_GT1_GT1 | 0.001 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | 0.049 | 49
SHELLG3_3020 | 0.001 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | 0.03 | 30
SHELLG3_3020 | 0.001 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | 0.039 | 39
SHELLG2 | 0.001 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | 0.072 | 72
SHELLG1_3015 | 0.001 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | 0.071 | 71
PSG_GT3_8060 | 0.001 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.164 | 164
PSG_GT2_8040 | 0.001 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.164 | 164
PSG_GN2_8050 | 0.001 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | 0.178 | 178
GBY_83841065 | 0.001 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | 0.02 | 20
EXN_14GT | 0.001 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | 0.14 | 140
GBY_83841065 | 0.001 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | 0.02 | 20
GBY_81821075 | 0.001 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | 0.02 | 20
GBY_81821075 | 0.001 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.048 | 48
GBY_73741085 | 0.001 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | 0.047 | 47
GBY_73741085 | 0.001 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.048 | 48
EP_1_2 | 0.001 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | 0.021 | 21
EP_1_2 | 0.001 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | 0.005 | 5
DPEC_GT45070 | 0.001 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | 0.158 | 158
DPEC_GT35010 | 0.001 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | 0.16 | 160
DPEC_GT25025 | 0.001 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | 0.156 | 156
DIB_GT3_8090 | 0.001 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | 0.0772 | 77.2
DIB_ST1_8085 | 0.001 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | 0.069 | 69
DIB_GT2_8075 | 0.001 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.065 | 65
DIB_GT1_8080 | 0.001 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | 0.064 | 64
CHE_GN4_8025 | 0.001 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | 0.142 | 142
CHE_GT1_8015 | 0.001 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | 0.173 | 173
CBY_GN1_1 | 0.001 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | 0.748 | 748
CAL_ST1_8000 | 0.001 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.065 | 65
CAL_GT1_8045 | 0.001 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | 0.152 | 152
DPEC_ST55065 | 0.001 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | 0.282 | 282
LPE_GT4_8085 | 0.001 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.041 | 41
LPE_GT3_8080 | 0.001 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.041 | 41
LPE_GT2_8075 | 0.001 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.042 | 42
LPE_GT1_8070 | 0.001 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.042 | 42
APD_GT1_8005 | 0.001 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | 0.14 | 140
CBY_GN2_2 | 0.001 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | 0.751 | 751
DPEC_GT15040 | 0.001 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | 0.162 | 162
EXN_15GT | 0.001 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | 0.033 | 33
EXN941GT | 0.001 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.019 | 19
EXN945GT | 0.001 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | 0.019 | 19
EXN943GT | 0.001 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.019 | 19
THW_3132 | 0.001 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.057 | 57
PR_GT1__9040 | 0.001 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | 0.035 | 35
WAPGT21_GT1 | 0.002 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
WAP_GN5_5 | 0.002 | 48925 | 5 | HOUSTON | YES | 216.6 | 278 | 657 | 0 | 1 | 0 | 0 | 0
WAP_GN3_3 | 0.002 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | 0.452 | 226
WAP_GN2_2 | 0.002 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | 0.2444 | 122.2
WAP_GN1_1 | 0.002 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | 0.249 | 124.5
PHR_GN2_2 | 0.002 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
CTL_GN2_8155 | 0.002 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | 0.022 | 11
CTL_GN1_8145 | 0.002 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | 0.11 | 55
CTL_GT4_8140 | 0.002 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | 0.188 | 94
CTL_GT3_8135 | 0.002 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | 0.182 | 91
CTL_GT2_8130 | 0.002 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | 0.206 | 103
BYU_GT4_8065 | 0.002 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.13 | 65
BYU_GT3_8060 | 0.002 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | 0.134 | 67
BYU_GT2_8055 | 0.002 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | 0.124 | 62
BYU_GT1_8075 | 0.002 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.13 | 65
TNDOWCGNGG8 | 0.002 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | 0.06 | 30
TNDOWCGNSG8 | 0.002 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | 0.064 | 32
TNSLCGN1__8 | 0.002 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | 0.06 | 30
TNTXCTY4CG8 | 0.002 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | 0.206 | 103
TNTXCTY3CG8 | 0.002 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | 0.17 | 85
TNTXCTY2CG8 | 0.002 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | 0.204 | 102
TNTXCTY1CG8 | 0.002 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | 0.21 | 105
TNBP_CGN4_8 | 0.002 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | 0.08 | 40
TNBPAMCG4_8 | 0.002 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | 0.192 | 96
TNBPAMCG3_8 | 0.002 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | 0.304 | 152
TNBPAMCG2_8 | 0.002 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | 0.3 | 150
TNBPAMCG1_8 | 0.002 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | 0.31 | 155
TNBP_CGN3_8 | 0.002 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | 0.106 | 53
TNBP_CGN2_8 | 0.002 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | 0.132 | 66
TNBP_CGN1_8 | 0.002 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | 0.12 | 60
WAP_GN4_4 | 0.002 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | 1.088 | 544
WAP_GN8_8 | 0.003 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
WAP_GN7_7 | 0.003 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN6_6 | 0.003 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
BVE_ST1_GN1 | 0.003 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | 0.738 | 246
BVE_GT2_5035 | 0.003 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | 0.51 | 170
BVE_GT1_GT1 | 0.003 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | 0.516 | 172
MNS_GT | 0.004 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | 0.1844 | 46.1
AK_GT1__8040 | 0.004 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | 0.136 | 34
TNSCLP3___8 | 0.005 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | 0.555 | 111
TNSCLP4___8 | 0.005 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | 0.575 | 115
TNSCLP2___8 | 0.005 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | 0.585 | 117
TNSCLP1___8 | 0.005 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | 0.58 | 116
BSF_GT1_8070 | 0.007 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | 0.07 | 10
BSF_GT1_8070 | 0.007 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | 0.504 | 72
DOW41000 | 0.008 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW39100 | 0.008 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
DOW38200 | 0.008 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW17000 | 0.008 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
CBE_ST34 | 0.008 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0.828 | 103.5
CBE_GT4 | 0.008 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.688 | 86
CBE_GT3 | 0.008 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.688 | 86
CBE_ST12 | 0.008 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0.828 | 103.5
CBE_GT2 | 0.008 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.688 | 86
CBE_GT1 | 0.008 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.688 | 86
DOW65000 | 0.008 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
DOW67000 | 0.008 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW38300 | 0.008 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
DOW38100 | 0.008 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
DOW42000 | 0.008 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
DOW49000 | 0.008 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
DOW63000 | 0.008 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
DOW82000 | 0.008 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW61000 | 0.008 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
DOW39200 | 0.008 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
DOW84000 | 0.008 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
DOW83000 | 0.008 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW81000 | 0.008 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
DOW66000 | 0.008 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
DOW64000 | 0.008 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
DOW62000 | 0.008 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
TGF_GT1_8000 | 0.009 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | 0.6228 | 69.2
STP_GN2___2 | 0.013 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
STP_GN1___1 | 0.013 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
CUECPL2A | 0.023 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | 0.276 | 12
FOR_5 | 0.03 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | 2.025 | 67.5
FOR_4 | 0.03 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | 2.238 | 74.6
FOR_3 | 0.03 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | 1.974 | 65.8
FOR_2 | 0.03 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | 1.974 | 65.8
FOR_1 | 0.03 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | 1.692 | 56.4
FOR_10 | 0.03 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | 2.19 | 73
FOR_9 | 0.03 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | 0.96 | 32
FOR_8 | 0.03 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | 0.84 | 28
FOR_7 | 0.03 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | 1.38 | 46
FOR_6 | 0.03 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | 0.78 | 26
ALCOA_G | 0.031 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
UCAR_1 | 0.033 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | 0.231 | 7
UCAR_2 | 0.033 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | 0.693 | 21
CSDR56 | 0.033 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 1.287 | 39
CSDR56 | 0.033 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.495 | 15
VISTRONG1 | 0.033 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
CSDR11 | 0.033 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | 1.287 | 39
CSDR7 | 0.033 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | 0.231 | 7
VISTRONG2 | 0.033 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
AIRCO_G | 0.033 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
CSDR89 | 0.033 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.495 | 15
CSDR89 | 0.033 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 1.287 | 39
DUP1V_1 | 0.034 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | 2.482 | 73
AMISTADHDRO2 | 0.034 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | 0.442 | 13
AMISTADHDRO1 | 0.034 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | 0.561 | 16.5
L_LAKEWO9_1Y | 0.034 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_LAKEWO9_1Y | 0.034 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
HAMILTON | 0.034 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
RAYBURNGEN2 | 0.035 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN1 | 0.035 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN3 | 0.035 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0.217 | 6.2
RAYBURNCC8 | 0.036 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 1.8 | 50
RAYBURNCC7 | 0.036 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 1.764 | 49
RAYBURNCC10 | 0.036 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 1.44 | 40
RAYBURNCC9 | 0.036 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 1.8 | 50
ELPS | 0.04 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | 0.24 | 6
EPLVT1 | 0.041 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
ICPGN#3 | 0.041 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 5.207 | 127
REYSHR_G | 0.041 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
ICPGN#2 | 0.041 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 6.15 | 150
ICPGN#1 | 0.041 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 6.109 | 149
LGEGN#3 | 0.041 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 3.731 | 91
LGEGN#2 | 0.041 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 6.273 | 153
LGEGN#1 | 0.041 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 6.478 | 158
CNOPST1 | 0.042 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 6.426 | 153
CNOPGT2 | 0.042 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 6.93 | 165
CNOPGT1 | 0.042 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 6.888 | 164
STARCO_1 | 0.042 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 1.596 | 38
VAL_2 | 0.042 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 1.05 | 25
VAL_1 | 0.042 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 1.05 | 25
KOCHREF2 | 0.042 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 1.596 | 38
DAV_2 | 0.042 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 14.28 | 340
DAV_1 | 0.042 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 14.238 | 339
COSW_2 | 0.042 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0.588 | 14
COSW_1 | 0.042 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0.84 | 20
MVGN#1 | 0.043 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 9.03 | 210
SI_RAY10 | 0.043 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 2.021 | 47
SI_RAY5 | 0.043 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0.43 | 10
SI_RAY6 | 0.043 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0.817 | 19
SI_RAY9 | 0.043 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 1.634 | 38
HECN3 | 0.043 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 7.267 | 169
HECN2 | 0.043 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 6.364 | 148
HECN1 | 0.043 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 6.364 | 148
MVGN#3 | 0.043 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 11.051 | 257
MVGN#2 | 0.043 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 8.815 | 205
SLURR | 0.043 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
MILHWYS | 0.043 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
CEL_B_1 | 0.043 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 1.247 | 29
CLO_1 | 0.043 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
FALCONHYDRO1 | 0.044 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.132 | 3
FALCONHYDRO3 | 0.044 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | 0.1232 | 2.8
FALCONHYDRO2 | 0.044 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.132 | 3
FALFURRI | 0.044 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
FGNTS201 | 0.044 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 7.568 | 172
FGNTS101 | 0.044 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 6.424 | 146
FGNTS001 | 0.044 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 6.248 | 142
ZAPATA | 0.045 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
BEEVILLE | 0.045 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
CIDINDUS | 0.046 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
LAR | 0.046 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
LAR_3 | 0.046 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | 3.6248 | 78.8
LAR_2 | 0.046 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | 0.414 | 9
LAR_1 | 0.046 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | 0.736 | 16
PEARSALLGEN3 | 0.055 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | 0.341 | 6.2
PEARSALLGEN2 | 0.055 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.341 | 6.2
PEARSALLGEN1 | 0.055 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.341 | 6.2
SANMIGUELGEN | 0.059 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
JKS1 | 0.063 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
AVR1_CT2 | 0.064 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | 9.28 | 145
AVR1_ST1 | 0.064 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | 10.496 | 164
AVR1_CT1 | 0.064 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | 9.6 | 150
LCPCT4 | 0.064 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 2.88 | 45
LCPCT3 | 0.064 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | 2.816 | 44
LCPCT2 | 0.064 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | 2.944 | 46
LCPCT1 | 0.064 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 2.88 | 45
LCP4 | 0.064 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | 6.08 | 95
LCP3 | 0.064 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | 3.712 | 58
OWS2 | 0.065 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | 24.635 | 379
OWS1 | 0.065 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | 27.105 | 417
VHB3 | 0.065 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | 25.805 | 397
VHB2 | 0.065 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | 14.3 | 220
VHB1 | 0.065 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | 13.39 | 206
JTD2 | 0.066 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
JTD1 | 0.066 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
WBT4 | 0.067 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | 10.117 | 151
WBT3 | 0.067 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | 6.432 | 96
WBT2 | 0.067 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | 5.36 | 80
WBT1 | 0.067 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | 1.7085 | 25.5
L_GUADGE1_6Y | 0.07 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | 14.28 | 204
L_GUADGE1_5Y | 0.07 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | 12.81 | 183
L_GUADGE1_4Y | 0.07 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | 10.43 | 149
L_GUADGE1_3Y | 0.07 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | 10.22 | 146
L_GUADGE1_2Y | 0.07 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | 9.73 | 139
L_GUADGE1_1Y | 0.07 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | 10.57 | 151
L_MCQUEE9_1Y | 0.075 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.075 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.075 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_RIONOG1S1Y | 0.076 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | 22.268 | 293
L_RIONOG1G3Y | 0.076 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | 11.4 | 150
L_RIONOG1G2Y | 0.076 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | 11.248 | 148
L_RIONOG1G1Y | 0.076 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | 11.172 | 147
L_HAYSEN1_4Y | 0.079 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | 18.091 | 229
L_HAYSEN1_3Y | 0.079 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | 17.854 | 226
L_HAYSEN1_2Y | 0.079 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | 17.696 | 224
L_HAYSEN1_1Y | 0.079 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | 17.617 | 223
L_SCHUMA8_1Y | 0.085 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
L_CANYHY8_1Y | 0.196 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0

## 3
Generator Sensitivities
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
LAKE_CRK1_G | -0.018 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -0.6372 | 35.4 |  | Sum GSF*Pgen
LAKE_CRK2_G | -0.018 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -4.086 | 227 | HOUSTON | 5.6594
THOUSE_2G | -0.017 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -13.685 | 805 | NORTH | -145.9047
THOUSE_1G | -0.017 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -9.571 | 563 | SOUTH | 171.5194
BOSQUESW501 | -0.016 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -2.416 | 151 | WEST | 2.0476
BOSQUESW804 | -0.016 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -1.328 | 83
BOSQUESW803 | -0.016 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -2.304 | 144 |  | Sum Pgen
BOSQUESW502 | -0.016 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -2.384 | 149 | HOUSTON | 13825.3
WHITNYDM01 | -0.014 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.21 | 15 | NORTH | 19200.9
WHITNYDM02 | -0.014 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.21 | 15 | SOUTH | 13890.7
SANDOW_4G | -0.01 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 |  | 1.029 | 0 | 0 | 0 | WEST | 4928.9
MDLTHELP_6G | -0.008 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -1.832 | 229
BBRN_1G | -0.008 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
ENNSTRAC_1G | -0.008 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -1.568 | 196 |  | AWGSF
ENNSTRAC_2G | -0.008 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -0.928 | 116 | HOUSTON | 0.00040935
MDLTHELP_1G | -0.008 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.72 | 215 | NORTH | -0.0075988
MDLTHELP_5G | -0.008 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -1.8 | 225 | SOUTH | 0.012348
MDLTHELP_4G | -0.008 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -1.712 | 214 | WEST | 0.00041543
MDLTHELP_2G | -0.008 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.72 | 215
BBRN_2G | -0.008 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
MDLTHELP_3G | -0.008 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.72 | 215 | N to H | -0.0080082
TRINIDAD_6G | -0.008 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -1.808 | 226 | N to S | -0.019947
KMICHICT4_G | -0.007 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -0.952 | 136 | W to N | 0.0080143
CHAMPION_1G | -0.007 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
FPLEFR1A_G | -0.007 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.19 | 170
TGATEWAY_4G | -0.007 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -2.793 | 399
LAMARPWR_5G | -0.007 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -1.141 | 163
KMICHICT2_G | -0.007 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -1.008 | 144
VALLEY_3G | -0.007 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -1.3034 | 186.2
MTCK3_G | -0.007 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
LKHB1_G | -0.007 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
HANDLEY_4G | -0.007 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -1.5225 | 217.5
STEAM1 | -0.007 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
CALFREST_2G | -0.007 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -1.085 | 155
KMICHICT5_G | -0.007 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -0.966 | 138
KMICHICT1_G | -0.007 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -0.994 | 142
NTHLK3_G | -0.007 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -1.7318 | 247.4
STEAM2 | -0.007 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.182 | 26
KMICHIST3_G | -0.007 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -2.17 | 310
FPLEFR2C_G | -0.007 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -1.134 | 162
KMICHIST6_G | -0.007 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -2.121 | 303
MOSES_3G | -0.007 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0
TGATEWAY_1G | -0.007 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -1.043 | 149
MARTLAKE_2G | -0.007 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
NTHLK2_G | -0.007 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
LEG_2___2 | -0.007 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
OLINGER_G1 | -0.007 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -0.4417 | 63.1
LAMARPWR_2G | -0.007 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -1.085 | 155
DENISNDM | -0.007 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.28 | 40
LAMARPWR_3G | -0.007 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.393 | 199
JNSNCNTY802 | -0.007 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -1.176 | 168
MARTLAKE_1G | -0.007 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
CALFREST_4G | -0.007 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -1.092 | 156
STRYKER_2G | -0.007 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -3.388 | 484
LKHB2_G | -0.007 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -3.598 | 514
VALLLEY_1G | -0.007 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -0.98 | 140
NTHLK1_G | -0.007 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
VALLEY_2G | -0.007 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -3.689 | 527
CALFREST_5G | -0.007 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -1.099 | 157
NEWMAN_G5 | -0.007 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
PEC_1G | -0.007 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -0.56 | 80
LAMARPWR_1G | -0.007 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -1.078 | 154
LAMARPWR_6G | -0.007 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.393 | 199
OLINGER_G2 | -0.007 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -0.6069 | 86.7
HANDLEY_2G | -0.007 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
FPLEFR1B_G | -0.007 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -1.099 | 157
FPLEFR2A_G | -0.007 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.19 | 170
OLINGER_G4 | -0.007 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.4137 | 59.1
MTCK6_G | -0.007 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
OLINGER_G3 | -0.007 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -0.8281 | 118.3
JNSNCNTY802 | -0.007 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -0.63 | 90
HANDLEY_5G | -0.007 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
FPLEFR1C_G | -0.007 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -1.113 | 159
COLLIN_1G | -0.007 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
LEG_1___1 | -0.007 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
MTCK7_G | -0.007 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
FPLEFR2S_G | -0.007 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -2.884 | 412
DCEAST | -0.007 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -2.8021 | 400.3
MTCK8_G | -0.007 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -3.339 | 477
TGATEWAY_2G | -0.007 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -0.896 | 128
MOSES_2G | -0.007 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
PEC_3G | -0.007 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -0.637 | 91
HANDLEY_3G | -0.007 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -2.4738 | 353.4
MOSES_1G | -0.007 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
FPLEFR2B_G | -0.007 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -1.12 | 160
TGATEWAY_3G | -0.007 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -1.022 | 146
STEAM3 | -0.007 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.287 | 41
MTCK2_G | -0.007 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
CALFREST_3G | -0.007 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -1.218 | 174
CALFREST_6G | -0.007 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -1.232 | 176
FPLEFR1S_G | -0.007 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -2.898 | 414
MARTLAKE_3G | -0.007 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
STRYKER_1G | -0.007 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -0.9835 | 140.5
LAMARPWR_4G | -0.007 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -1.148 | 164
HANDLEY_1G | -0.007 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
DENISNDM | -0.007 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.28 | 40
CALFREST_1G | -0.007 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -1.064 | 152
PEC_2G | -0.007 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -0.588 | 84
SPENCER_G4 | -0.006 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.288 | 48
TNTNPONE_28 | -0.006 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
ATKINS4 | -0.006 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0
DANSBY2 | -0.006 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | -0.276 | 46
EAGLEMNT_1G | -0.006 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
EAGLEMNT_3G | -0.006 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
DANSBY14 | -0.006 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | -0.486 | 81
TNTNPONE_18 | -0.006 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
EAGLEMNT_2G | -0.006 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
ATKINS7 | -0.006 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0
ATKINS6 | -0.006 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0
ATKINS3 | -0.006 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0
ATKINS5 | -0.006 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0
SPENCER_G5 | -0.006 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.312 | 52
DECRDOVA_4G | -0.005 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.325 | 65
NTHTEXAS01 | -0.005 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.025 | 5
TAMUGEN1 | -0.005 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | -0.16 | 32
DECRDOVA_1G | -0.005 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -3.895 | 779
DECRDOVA_3G | -0.005 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.325 | 65
WLFHOLW_2G | -0.005 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -1.095 | 219
NTHTEXAS03 | -0.005 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.075 | 15
DECRDOVA_2G | -0.005 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -0.325 | 65
NTHTEXAS02 | -0.005 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.025 | 5
DECRDOVA_5G | -0.005 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.325 | 65
COMCHEPK_1G | -0.005 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
JCKCNTY803 | -0.005 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -0.735 | 147
JCKCNTY802 | -0.005 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -0.735 | 147
JCKCNTY801 | -0.005 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -1.44 | 288
WLFHOLW_1G | -0.005 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -1.08 | 216
COMCHEPK_2G | -0.005 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
WLFHOLW_3G | -0.005 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -1.34 | 268
FTR_GT2_5110 | -0.004 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | -0.636 | 159
FTR_GT1_5105 | -0.004 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | -0.624 | 156
FTR_CN4_5095 | -0.004 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | -1.52 | 380
FTR_GT3_5085 | -0.004 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | -0.632 | 158
MRSSHPRD | -0.004 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.048 | 12
MRSSHPRD01 | -0.004 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.048 | 12
WCPWRCO_3G | -0.004 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -0.968 | 242
WCPWRCO_2G | -0.004 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -0.816 | 204
WCPWRCO_1G | -0.004 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -0.816 | 204
GIBN_CREK_G1 | -0.004 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
RWMILLER05 | -0.003 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -0.303 | 101
BARTNWND_1G | -0.003 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.036 | 12
WFCOGEN_2G | -0.003 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.036 | 12
RWMILLER04 | -0.003 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -0.306 | 102
WFCOGEN_2G | -0.003 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.036 | 12
WFCOGEN_1G | -0.003 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.036 | 12
WFCOGEN_1G | -0.003 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.036 | 12
RWMILLER03 | -0.003 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -0.468 | 156
GRHAMSES_1G | -0.003 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -0.726 | 242
GRHAMSES_2G | -0.003 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -1.107 | 369
RWMILLER01 | -0.003 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -0.225 | 75
RWMILLER02 | -0.003 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -0.357 | 119
OKLA7A | -0.002 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.1 | 50
OKLAUN1G | -0.002 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
CVC_GT2_5020 | -0.001 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | -0.159 | 159
CVC_GT1_5035 | -0.001 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | -0.155 | 155
CHE_GT2_5030 | -0.001 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | -0.173 | 173
CVC_GT3_5045 | -0.001 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | -0.158 | 158
CVC_ST5_5040 | -0.001 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | -0.133 | 133
DPEC_ST55065 | 0 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | 0 | 282
EXN_GT | 0 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | 0 | 81
EXN942GT | 0 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | 0 | 20
EXN945GT | 0 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | 0 | 19
EXN944GT | 0 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | 0 | 33
EXN943GT | 0 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0 | 19
THW_5152 | 0 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
THW_5556 | 0 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
THW_5152 | 0 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
THW_4344 | 0 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0 | 58
THW_3334 | 0 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0 | 58
THW_3132 | 0 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0 | 57
THW_ST3_ST_3 | 0 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | 0 | 110
SRB_GN3_3 | 0 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | 0 | 220
SRB_GN1_1 | 0 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | 0 | 176
SJS_GT2_GT2 | 0 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | 0 | 49
SHELLG3_3020 | 0 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | 0 | 30
SHELLG3_3020 | 0 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | 0 | 39
SHELLG2 | 0 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | 0 | 72
CVC_GT4_8005 | 0 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | 0 | 165
SRB_GT211035 | 0 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
PSA_GN1_8165 | 0 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | 0 | 104
PSA_GT4_8145 | 0 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0 | 66
PSG_GT2_8040 | 0 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0 | 164
SWETWATR_3G | 0 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | 0 | 68
SWETWATR_4G | 0 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | 0 | 61
PSG_GN2_8050 | 0 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | 0 | 178
DPEC_GT15040 | 0 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | 0 | 162
GBY_83841065 | 0 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | 0 | 20
GBY_81821075 | 0 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | 0 | 20
GBY_73741085 | 0 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | 0 | 47
GBY_GN5_5 | 0 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | 0 | 298.5
DIB_GT1_8080 | 0 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | 0 | 64
EP_1_2 | 0 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | 0 | 5
DPEC_GT35010 | 0 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | 0 | 160
DPEC_GT25025 | 0 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | 0 | 156
ROSCOEW_5 | 0 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | 0 | 20.9
BTE_ST1_8070 | 0 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | 0 | 234
BTE_GT4_8055 | 0 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0 | 163
BTE_GT3_8045 | 0 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | 0 | 158
CHE_GN4_8025 | 0 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | 0 | 142
CHE_GT1_8015 | 0 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | 0 | 173
DIB_GT2_8075 | 0 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0 | 65
DIB_GT3_8090 | 0 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | 0 | 77.2
CBY_GN1_1 | 0 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | 0 | 748
DPEC_GT45070 | 0 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | 0 | 158
EP_1_2 | 0 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | 0 | 21
ROSCOEWI_5 | 0 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | 0 | 12.6
CTL_GN2_8155 | 0 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | 0 | 11
CTL_GN1_8145 | 0 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | 0 | 55
CTL_GT3_8135 | 0 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | 0 | 91
CTL_GT2_8130 | 0 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | 0 | 103
CAL_ST1_8000 | 0 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0 | 65
BYU_GT4_8065 | 0 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0 | 65
BYU_GT2_8055 | 0 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | 0 | 62
BTE_GT2_8075 | 0 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0 | 163
LPE_GT3_8080 | 0 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0 | 41
APD_GT1_8005 | 0 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | 0 | 140
PSG_GT3_8060 | 0 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0 | 164
PHR_GN2_2 | 0 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
PSA_GT1_8160 | 0 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | 0 | 65
PR_GT1__9040 | 0 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | 0 | 35
PSA_GT6_8135 | 0 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | 0 | 59
SLSTR1PP_1G | 0 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | 0 | 6
LPE_GT1_8070 | 0 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0 | 42
WILDHRS11A | 0 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | 0 | 12.6
PSA_GT5_8140 | 0 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | 0 | 64
DIB_ST1_8085 | 0 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | 0 | 69
WHRLWIND1A | 0 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | 0 | 6
PSA_GT2_8155 | 0 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0 | 66
LPE_GT4_8085 | 0 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0 | 41
SWETWATR_1G | 0 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | 0 | 30
PSA_GT3_8150 | 0 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | 0 | 70
SHELLG1_3015 | 0 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | 0 | 71
THW_3334 | 0 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0 | 58
THW_4142 | 0 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0 | 58
MESQUITW_2G | 0 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | 0 | 23.6
SWETWATR_2G | 0 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | 0 | 72
THW_5354 | 0 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0 | 16.4
THW_5354 | 0 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0 | 16.6
MESQUITW_1G | 0 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | 0 | 40
GBY_81821075 | 0 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0 | 48
SRB_GN2_2 | 0 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | 0 | 174
EXN_15GT | 0 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | 0 | 33
SOL_GT1 | 0 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | 0 | 16.2
SRB_GT211035 | 0 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
EXN_16GT | 0 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | 0 | 32
EXN938GT | 0 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | 0 | 43
THW_ST4_ST_4 | 0 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | 0 | 108
EXN_17GT | 0 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | 0 | 31
SRB_GN4_4 | 0 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | 0 | 226
THW_4142 | 0 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0 | 57
THW_3132 | 0 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0 | 57
EXN_14GT | 0 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | 0 | 140
THW_GT1_GT_1 | 0 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
THW_4344 | 0 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0 | 58
SJS_GT1_GT1 | 0 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | 0 | 49
THW_5556 | 0 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0 | 16.6
BYU_GT3_8060 | 0 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | 0 | 67
EXN941GT | 0 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0 | 19
GBY_73741085 | 0 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0 | 48
CAL_GT1_8045 | 0 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | 0 | 152
BYU_GT1_8075 | 0 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0 | 65
GBY_83841065 | 0 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | 0 | 20
CTL_GT4_8140 | 0 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | 0 | 94
CBY_GN2_2 | 0 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | 0 | 751
LPE_GT2_8075 | 0 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0 | 42
OCOTILLO_1G | 0.001 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | 0.0058 | 5.8
STANTONW_8 | 0.001 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | 0.0101 | 10.1
WAP_GN8_8 | 0.001 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
WAP_GN7_7 | 0.001 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN5_5 | 0.001 | 48925 | 5 | HOUSTON | YES | 216.7 | 278 | 657 | 0 | 1 | 0 | 0 | 0
WAP_GN4_4 | 0.001 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | 0.544 | 544
WAP_GN3_3 | 0.001 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | 0.226 | 226
WAP_GN1_1 | 0.001 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | 0.1245 | 124.5
BSP_1 | 0.001 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
WAP_GN2_2 | 0.001 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | 0.1222 | 122.2
AIRTRICITY_8 | 0.001 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | 0.018 | 18
MCDDONAL_8 | 0.001 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | 0.0214 | 21.4
KINDERMG_3G | 0.001 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
L_SWEETW1_3N | 0.001 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | 0.0178 | 17.8
KINDERMG_2G | 0.001 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
L_DELAWA1_1Y | 0.001 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | 0.0045 | 4.5
KINDERMG_1G | 0.001 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
L_DELAWA1_1Y | 0.001 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | 0.0052 | 5.2
SCURRYCW_1G | 0.001 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | 0.0141 | 14.1
PBCTCGE_3G | 0.001 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | 0.062 | 62
CIELOGEN_2G | 0.001 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | 0.0061 | 6.1
MNS_GT | 0.001 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | 0.0461 | 46.1
CIELOGEN_1G | 0.001 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | 0.0099 | 9.9
LONGSHORT_5 | 0.001 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | 0.015 | 15
TRENTIPP_8 | 0.001 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | 0.0225 | 22.5
CALENG3G_3G | 0.001 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | 0.069 | 69
SNYDERW1A | 0.001 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | 0.0063 | 6.3
CALENG2G_2G | 0.001 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | 0.074 | 74
L_SWEETW1_1N | 0.001 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | 0.0161 | 16.1
TNBPAMCG4_8 | 0.001 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | 0.096 | 96
BVE_ST1_GN1 | 0.001 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | 0.246 | 246
BVE_GT1_GT1 | 0.001 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | 0.172 | 172
CALENG1G_1G | 0.001 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | 0.073 | 73
TNSLCGN1__8 | 0.001 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | 0.03 | 30
MRGNFG_6G | 0.001 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | 0.066 | 66
AK_GT1__8040 | 0.001 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | 0.034 | 34
TNTXCTY4CG8 | 0.001 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | 0.103 | 103
TNDOWCGNGG8 | 0.001 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | 0.03 | 30
TNDOWCGNSG8 | 0.001 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | 0.032 | 32
MRGNEG_5G | 0.001 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | 0.068 | 68
TNTXCTY3CG8 | 0.001 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | 0.085 | 85
TNTXCTY2CG8 | 0.001 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | 0.102 | 102
TNBP_CGN4_8 | 0.001 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | 0.04 | 40
TNBPAMCG3_8 | 0.001 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | 0.152 | 152
MRGNDG_4G | 0.001 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | 0.07 | 70
TNBPAMCG2_8 | 0.001 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | 0.15 | 150
TNBPAMCG1_8 | 0.001 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | 0.155 | 155
TNBP_CGN3_8 | 0.001 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | 0.053 | 53
TNBP_CGN2_8 | 0.001 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | 0.066 | 66
TNBP_CGN1_8 | 0.001 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | 0.06 | 60
RDCNYNG1 | 0.001 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | 0.0084 | 8.4
MRGNCG_3G | 0.001 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | 0.07 | 70
MRGNBG_2G | 0.001 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | 0.071 | 71
PBCTAGE_1G | 0.001 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | 0.064 | 64
MRGNAG_1G | 0.001 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | 0.069 | 69
MORGAN5G_5G | 0.001 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | 0.137 | 137
AEPWIND_8 | 0.001 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | 0.0152 | 15.2
TIEHVSG_2G | 0.001 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | 0.211 | 211
PB6GEN_7G | 0.001 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | 0.515 | 515
TIEHVCG_4G | 0.001 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | 0.149 | 149
TIEHVCG_3G | 0.001 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | 0.132 | 132
TIEHVCG_2G | 0.001 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | 0.132 | 132
TIEHVCG_1G | 0.001 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | 0.145 | 145
L_BITTCR1_1N | 0.001 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | 0.0056 | 5.6
TIEHVSG_1G | 0.001 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | 0.211 | 211
NAV6ST | 0.001 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | 0.115 | 115
NAV5CT | 0.001 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | 0.08 | 80
NAV4CT | 0.001 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | 0.08 | 80
PB5GEN_6G | 0.001 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | 0.115 | 115
NAV3ST | 0.001 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | 0.115 | 115
NAV2CT | 0.001 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | 0.08 | 80
NAV1CT | 0.001 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | 0.08 | 80
PBCTBGE_2G | 0.001 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | 0.065 | 65
PBCTEGE_5G | 0.001 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | 0.065 | 65
L_SWEETW1_4N | 0.001 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | 0.0157 | 15.7
PBCTDGE_4G | 0.001 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | 0.065 | 65
WAPGT21_GT1 | 0.001 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
L_SWEETW1_2N | 0.001 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | 0.0203 | 20.3
WAP_GN6_6 | 0.001 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
BVE_GT2_5035 | 0.001 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | 0.17 | 170
TNTXCTY1CG8 | 0.001 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | 0.105 | 105
DOW41000 | 0.002 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW39100 | 0.002 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
DOW38200 | 0.002 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW17000 | 0.002 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
DOW38300 | 0.002 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
DOW39200 | 0.002 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
DOW82000 | 0.002 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW38100 | 0.002 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
DOW49000 | 0.002 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
DOW42000 | 0.002 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
DOW84000 | 0.002 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
SWMESA | 0.002 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | 0.0224 | 11.2
BSF_GT1_8070 | 0.002 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | 0.02 | 10
BSF_GT1_8070 | 0.002 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | 0.144 | 72
TNSCLP3___8 | 0.002 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | 0.222 | 111
TNSCLP4___8 | 0.002 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | 0.23 | 115
TNSCLP2___8 | 0.002 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | 0.234 | 117
TNSCLP1___8 | 0.002 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | 0.232 | 116
KM NEP | 0.002 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | 0.024 | 12
DOW65000 | 0.002 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
DOW63000 | 0.002 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
TNWDWRDU2_8 | 0.002 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | 0.024 | 12
WDWDU1 | 0.002 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | 0.024 | 12
KM SWP | 0.002 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | 0.024 | 12
NWPWRG1_1G | 0.002 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | 0.0068 | 3.4
CIRELLO | 0.002 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | 0.07 | 35
HORSH3 | 0.002 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | 0.0672 | 33.6
RIO_DRCS | 0.002 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
HORSH1 | 0.002 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | 0.0666 | 33.3
L_DIVIDE1_1N | 0.002 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | 0.053 | 26.5
LOUIS1A | 0.002 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | 0.051 | 25.5
L_GASCCR1_1N | 0.002 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | 0.03 | 15
HORSH4 | 0.002 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | 0.0344 | 17.2
HORSH2 | 0.002 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | 0.0552 | 27.6
BUFGGEN | 0.002 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | 0.036 | 18
KM NWP | 0.002 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | 0.024 | 12
KM SEP | 0.002 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | 0.012 | 6
WESTXWIN_1G | 0.002 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | 0.0014 | 0.7
DOW83000 | 0.002 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW61000 | 0.002 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
DOW81000 | 0.002 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
DOW67000 | 0.002 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW66000 | 0.002 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
DOW64000 | 0.002 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
DOW62000 | 0.002 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
TGF_GT1_8000 | 0.003 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | 0.2076 | 69.2
CALHN_G1 | 0.003 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | 0.0513 | 17.1
DSKY1 | 0.003 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | 0.0378 | 12.6
ORNNWP1 | 0.003 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | 0.036 | 12
DSKY2 | 0.003 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | 0.0345 | 11.5
CBE_ST34 | 0.004 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0.414 | 103.5
CBE_GT4 | 0.004 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.344 | 86
CBE_GT3 | 0.004 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.344 | 86
CBE_ST12 | 0.004 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0.414 | 103.5
CBE_GT2 | 0.004 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.344 | 86
CBE_GT1 | 0.004 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.344 | 86
STP_GN2___2 | 0.004 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
STP_GN1___1 | 0.004 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
FRNDDRCS | 0.004 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
L_LOSTPI1_3Y | 0.006 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | 1.0434 | 173.9
L_LOSTPI1_2Y | 0.006 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | 0.9462 | 157.7
L_LOSTPI1_1Y | 0.006 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | 0.9522 | 158.7
FOR_5 | 0.007 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | 0.4725 | 67.5
FOR_4 | 0.007 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | 0.5222 | 74.6
FOR_3 | 0.007 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | 0.4606 | 65.8
FOR_2 | 0.007 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | 0.4606 | 65.8
FOR_1 | 0.007 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | 0.3948 | 56.4
ALCOA_G | 0.007 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
L_FPPYD21_3Y | 0.007 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_2Y | 0.007 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_1Y | 0.007 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0
FOR_10 | 0.007 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | 0.511 | 73
FOR_9 | 0.007 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | 0.224 | 32
FOR_8 | 0.007 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | 0.196 | 28
FOR_7 | 0.007 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | 0.322 | 46
FOR_6 | 0.007 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | 0.182 | 26
UCAR_1 | 0.008 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | 0.056 | 7
UCAR_2 | 0.008 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | 0.168 | 21
DUP1V_1 | 0.008 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | 0.584 | 73
L_BASTEN1_3Y | 0.008 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | 1.816 | 227
L_BASTEN1_2Y | 0.008 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | 1.168 | 146
L_BASTEN1_1Y | 0.008 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | 1.176 | 147
CSDR56 | 0.008 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.312 | 39
FALFURRI | 0.008 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
FGNTS201 | 0.008 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 1.376 | 172
VISTRONG2 | 0.008 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
VISTRONG1 | 0.008 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
REYSHR_G | 0.008 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
SI_RAY10 | 0.008 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 0.376 | 47
SI_RAY5 | 0.008 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0.08 | 10
SI_RAY6 | 0.008 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0.152 | 19
SI_RAY9 | 0.008 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 0.304 | 38
RAYBURNCC8 | 0.008 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.4 | 50
RAYBURNCC7 | 0.008 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 0.392 | 49
RAYBURNCC10 | 0.008 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 0.32 | 40
RAYBURNCC9 | 0.008 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.4 | 50
RAYBURNGEN2 | 0.008 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN1 | 0.008 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN3 | 0.008 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0.0496 | 6.2
CSDR7 | 0.008 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | 0.056 | 7
CSDR56 | 0.008 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.12 | 15
HECN3 | 0.008 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 1.352 | 169
HECN2 | 0.008 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 1.184 | 148
HECN1 | 0.008 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 1.184 | 148
MVGN#3 | 0.008 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 2.056 | 257
MVGN#2 | 0.008 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 1.64 | 205
MVGN#1 | 0.008 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 1.68 | 210
SLURR | 0.008 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
FGNTS101 | 0.008 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 1.168 | 146
AIRCO_G | 0.008 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
FGNTS001 | 0.008 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 1.136 | 142
ICPGN#3 | 0.008 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 1.016 | 127
CSDR11 | 0.008 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | 0.312 | 39
ICPGN#2 | 0.008 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 1.2 | 150
ICPGN#1 | 0.008 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 1.192 | 149
CSDR89 | 0.008 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.12 | 15
LGEGN#3 | 0.008 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 0.728 | 91
CSDR89 | 0.008 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.312 | 39
LGEGN#2 | 0.008 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.224 | 153
LGEGN#1 | 0.008 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 1.264 | 158
CNOPST1 | 0.008 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.224 | 153
MILHWYS | 0.008 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
CNOPGT2 | 0.008 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 1.32 | 165
CNOPGT1 | 0.008 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 1.312 | 164
CEL_B_1 | 0.008 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 0.232 | 29
STARCO_1 | 0.008 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 0.304 | 38
VAL_2 | 0.008 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.2 | 25
VAL_1 | 0.008 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.2 | 25
KOCHREF2 | 0.008 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 0.304 | 38
DAV_2 | 0.008 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 2.72 | 340
DAV_1 | 0.008 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 2.712 | 339
COSW_2 | 0.008 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0.112 | 14
COSW_1 | 0.008 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0.16 | 20
FALCONHYDRO1 | 0.009 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.027 | 3
AMISTADHDRO2 | 0.009 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | 0.117 | 13
AMISTADHDRO1 | 0.009 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | 0.1485 | 16.5
FALCONHYDRO3 | 0.009 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | 0.0252 | 2.8
FALCONHYDRO2 | 0.009 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.027 | 3
ZAPATA | 0.009 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
HAMILTON | 0.009 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
BEEVILLE | 0.009 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
CIDINDUS | 0.009 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
LAR | 0.009 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
EPLVT1 | 0.009 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
LAR_3 | 0.009 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | 0.7092 | 78.8
LAR_2 | 0.009 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | 0.081 | 9
LAR_1 | 0.009 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | 0.144 | 16
ELPS | 0.009 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | 0.054 | 6
CLO_1 | 0.009 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
L_RIONOG1S1Y | 0.01 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | 2.93 | 293
L_RIONOG1G3Y | 0.01 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | 1.5 | 150
L_RIONOG1G2Y | 0.01 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | 1.48 | 148
L_RIONOG1G1Y | 0.01 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | 1.47 | 147
L_GUADGE1_6Y | 0.01 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | 2.04 | 204
L_GUADGE1_5Y | 0.01 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | 1.83 | 183
L_GUADGE1_4Y | 0.01 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | 1.49 | 149
L_GUADGE1_3Y | 0.01 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | 1.46 | 146
L_GUADGE1_2Y | 0.01 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | 1.39 | 139
L_GUADGE1_1Y | 0.01 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | 1.51 | 151
L_HAYSEN1_4Y | 0.01 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | 2.29 | 229
L_HAYSEN1_3Y | 0.01 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | 2.26 | 226
L_HAYSEN1_2Y | 0.01 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | 2.24 | 224
L_HAYSEN1_1Y | 0.01 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | 2.23 | 223
SANMIGUELGEN | 0.01 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
PEARSALLGEN3 | 0.01 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | 0.062 | 6.2
PEARSALLGEN2 | 0.01 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.062 | 6.2
PEARSALLGEN1 | 0.01 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.062 | 6.2
CUECPL2A | 0.01 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | 0.12 | 12
L_LAKEWO9_1Y | 0.011 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_LAKEWO9_1Y | 0.011 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_SCHUMA8_1Y | 0.011 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
L_SIMGID1_3Y | 0.011 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | 3.5739 | 324.9
L_SIMGID1_2Y | 0.011 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | 1.463 | 133
L_SIMGID1_1Y | 0.011 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | 1.463 | 133
AVR1_CT2 | 0.011 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | 1.595 | 145
AVR1_ST1 | 0.011 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | 1.804 | 164
AVR1_CT1 | 0.011 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | 1.65 | 150
WBT4 | 0.011 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | 1.661 | 151
WBT3 | 0.011 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | 1.056 | 96
WBT2 | 0.011 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | 0.88 | 80
WBT1 | 0.011 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | 0.2805 | 25.5
JKS1 | 0.011 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
OWS2 | 0.011 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | 4.169 | 379
OWS1 | 0.011 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | 4.587 | 417
LCPCT4 | 0.011 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 0.495 | 45
LCPCT3 | 0.011 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | 0.484 | 44
LCPCT2 | 0.011 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | 0.506 | 46
LCPCT1 | 0.011 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 0.495 | 45
LCP4 | 0.011 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | 1.045 | 95
LCP3 | 0.011 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | 0.638 | 58
JTD2 | 0.011 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
JTD1 | 0.011 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
VHB3 | 0.011 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | 4.367 | 397
VHB2 | 0.011 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | 2.42 | 220
VHB1 | 0.011 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | 2.266 | 206
L_MCQUEE9_1Y | 0.012 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.012 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.012 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
DECKR_G6 | 0.014 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | 0.616 | 44
DECKR_G5 | 0.014 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.616 | 44
DECKR_G4 | 0.014 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.616 | 44
DECKR_G3 | 0.014 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0
L_CANYHY8_1Y | 0.015 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0
SANDHG5C | 0.015 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | 2.1 | 140
SANDHG5A | 0.015 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | 2.25 | 150
SANDH_G4 | 0.015 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.675 | 45
SANDH_G3 | 0.015 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | 0.675 | 45
SANDH_G2 | 0.015 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.675 | 45
SANDH_G1 | 0.015 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | 0.675 | 45
DECKR_G2 | 0.015 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | 6 | 400
DECKR_G1 | 0.015 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | 4.8 | 320
L_AUSTPL1_1Y | 0.017 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.119 | 7
L_AUSTPL1_1Y | 0.017 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.119 | 7
L_MARSFO1G3Y | 0.035 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.77 | 22
L_MARSFO1G2Y | 0.035 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | 0.56 | 16
L_MARSFO1G1Y | 0.035 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.77 | 22
L_MARBFA1_2Y | 0.066 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | 0.858 | 13
L_MARBFA1_1Y | 0.066 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_FERGUS1_1Y | 0.082 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | 32.718 | 399
L_WIRTZ_1G2Y | 0.083 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | 1.494 | 18
L_WIRTZ_1G1Y | 0.083 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
L_INKSDA1_1Y | 0.112 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | 1.12 | 10
L_BUCHAN1_3Y | 0.123 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | 1.353 | 11
L_BUCHAN1_2Y | 0.123 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_1Y | 0.123 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | 1.722 | 14

## 4
Generator Sensitivities
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
LAKE_CRK1_G | -0.032 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -1.1328 | 35.4 |  | Sum GSF*Pgen
LAKE_CRK2_G | -0.032 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -7.264 | 227 | HOUSTON | 43.8004
THOUSE_1G | -0.031 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -17.453 | 563 | NORTH | -324.7488
THOUSE_2G | -0.031 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -24.955 | 805 | SOUTH | 337.3738
BOSQUESW502 | -0.03 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -4.47 | 149 | WEST | -38.3985
BOSQUESW501 | -0.03 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -4.53 | 151
BOSQUESW803 | -0.028 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -4.032 | 144 |  | Sum Pgen
BOSQUESW804 | -0.028 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -2.324 | 83 | HOUSTON | 13825.3
WHITNYDM01 | -0.026 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.39 | 15 | NORTH | 19200.9
WHITNYDM02 | -0.026 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.39 | 15 | SOUTH | 13890.7
MDLTHELP_2G | -0.018 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.87 | 215 | WEST | 4928.9
MDLTHELP_4G | -0.018 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -3.852 | 214
MDLTHELP_1G | -0.018 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.87 | 215
MDLTHELP_5G | -0.018 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -4.05 | 225 |  | AWGSF
MDLTHELP_3G | -0.018 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -3.87 | 215 | HOUSTON | 0.0031681
MDLTHELP_6G | -0.018 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -4.122 | 229 | NORTH | -0.016913
JNSNCNTY802 | -0.017 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -1.53 | 90 | SOUTH | 0.024288
TRINIDAD_6G | -0.017 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -3.842 | 226 | WEST | -0.0077905
JNSNCNTY802 | -0.017 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -2.856 | 168
ENNSTRAC_1G | -0.017 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -3.332 | 196
ENNSTRAC_2G | -0.017 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -1.972 | 116 | N to H | -0.020081
FPLEFR1C_G | -0.016 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -2.544 | 159 | N to S | -0.041201
MOSES_3G | -0.016 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0 | W to N | 0.0091227
LKHB2_G | -0.016 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -8.224 | 514
KMICHICT1_G | -0.016 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -2.272 | 142
DCEAST | -0.016 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -6.4048 | 400.3
OLINGER_G2 | -0.016 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -1.3872 | 86.7
KMICHICT4_G | -0.016 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -2.176 | 136
KMICHICT2_G | -0.016 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -2.304 | 144
KMICHIST3_G | -0.016 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -4.96 | 310
HANDLEY_4G | -0.016 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -3.48 | 217.5
FPLEFR2S_G | -0.016 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -6.592 | 412
VALLEY_3G | -0.016 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -2.9792 | 186.2
VALLLEY_1G | -0.016 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -2.24 | 140
OLINGER_G1 | -0.016 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -1.0096 | 63.1
VALLEY_2G | -0.016 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -8.432 | 527
FPLEFR2B_G | -0.016 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -2.56 | 160
STEAM2 | -0.016 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.416 | 26
HANDLEY_1G | -0.016 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
HANDLEY_2G | -0.016 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
TGATEWAY_3G | -0.016 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -2.336 | 146
MTCK3_G | -0.016 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
PEC_1G | -0.016 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -1.28 | 80
KMICHIST6_G | -0.016 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -4.848 | 303
MOSES_1G | -0.016 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
MOSES_2G | -0.016 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
CALFREST_5G | -0.016 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -2.512 | 157
MARTLAKE_3G | -0.016 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
TGATEWAY_2G | -0.016 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -2.048 | 128
NTHLK3_G | -0.016 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -3.9584 | 247.4
LAMARPWR_2G | -0.016 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -2.48 | 155
CALFREST_6G | -0.016 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -2.816 | 176
MARTLAKE_2G | -0.016 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
LKHB1_G | -0.016 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
DENISNDM | -0.016 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.64 | 40
MTCK7_G | -0.016 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
LAMARPWR_3G | -0.016 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -3.184 | 199
MARTLAKE_1G | -0.016 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
TGATEWAY_4G | -0.016 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -6.384 | 399
CALFREST_1G | -0.016 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -2.432 | 152
TGATEWAY_1G | -0.016 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -2.384 | 149
STRYKER_2G | -0.016 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -7.744 | 484
COLLIN_1G | -0.016 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
NTHLK2_G | -0.016 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
LAMARPWR_4G | -0.016 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -2.624 | 164
LAMARPWR_6G | -0.016 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -3.184 | 199
FPLEFR2C_G | -0.016 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -2.592 | 162
FPLEFR1A_G | -0.016 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -2.72 | 170
DENISNDM | -0.016 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.64 | 40
MTCK8_G | -0.016 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -7.632 | 477
FPLEFR1S_G | -0.016 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -6.624 | 414
NTHLK1_G | -0.016 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
KMICHICT5_G | -0.016 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -2.208 | 138
FPLEFR1B_G | -0.016 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -2.512 | 157
OLINGER_G4 | -0.016 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.9456 | 59.1
CHAMPION_1G | -0.016 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
CALFREST_3G | -0.016 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -2.784 | 174
CALFREST_2G | -0.016 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -2.48 | 155
STRYKER_1G | -0.016 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -2.248 | 140.5
STEAM1 | -0.016 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
FPLEFR2A_G | -0.016 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -2.72 | 170
HANDLEY_3G | -0.016 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -5.6544 | 353.4
LAMARPWR_1G | -0.016 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -2.464 | 154
CALFREST_4G | -0.016 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -2.496 | 156
OLINGER_G3 | -0.016 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -1.8928 | 118.3
STEAM3 | -0.016 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.656 | 41
LAMARPWR_5G | -0.016 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -2.608 | 163
MTCK6_G | -0.016 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
PEC_2G | -0.016 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -1.344 | 84
NEWMAN_G5 | -0.016 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
PEC_3G | -0.016 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -1.456 | 91
MTCK2_G | -0.016 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
HANDLEY_5G | -0.016 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
SPENCER_G4 | -0.015 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.72 | 48
DECRDOVA_2G | -0.015 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -0.975 | 65
EAGLEMNT_1G | -0.015 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
EAGLEMNT_3G | -0.015 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
SPENCER_G5 | -0.015 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.78 | 52
DECRDOVA_5G | -0.015 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.975 | 65
DECRDOVA_3G | -0.015 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.975 | 65
DECRDOVA_4G | -0.015 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.975 | 65
BBRN_2G | -0.015 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
DECRDOVA_1G | -0.015 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -11.685 | 779
BBRN_1G | -0.015 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
EAGLEMNT_2G | -0.015 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
LEG_1___1 | -0.014 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
LEG_2___2 | -0.014 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
WLFHOLW_1G | -0.014 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -3.024 | 216
COMCHEPK_2G | -0.014 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
WCPWRCO_3G | -0.014 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -3.388 | 242
WLFHOLW_3G | -0.014 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -3.752 | 268
WCPWRCO_1G | -0.014 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -2.856 | 204
COMCHEPK_1G | -0.014 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
JCKCNTY801 | -0.014 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -4.032 | 288
JCKCNTY803 | -0.014 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -2.058 | 147
NTHTEXAS01 | -0.014 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.07 | 5
WCPWRCO_2G | -0.014 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -2.856 | 204
JCKCNTY802 | -0.014 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -2.058 | 147
NTHTEXAS03 | -0.014 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.21 | 15
NTHTEXAS02 | -0.014 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.07 | 5
WLFHOLW_2G | -0.014 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -3.066 | 219
MRSSHPRD01 | -0.013 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.156 | 12
MRSSHPRD | -0.013 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.156 | 12
RWMILLER01 | -0.013 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -0.975 | 75
RWMILLER05 | -0.013 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -1.313 | 101
BARTNWND_1G | -0.013 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.156 | 12
RWMILLER04 | -0.013 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -1.326 | 102
RWMILLER02 | -0.013 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -1.547 | 119
RWMILLER03 | -0.013 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -2.028 | 156
TNTNPONE_18 | -0.012 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
WFCOGEN_2G | -0.012 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.144 | 12
WFCOGEN_2G | -0.012 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.144 | 12
WFCOGEN_1G | -0.012 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.144 | 12
WFCOGEN_1G | -0.012 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.144 | 12
TNTNPONE_28 | -0.012 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
GRHAMSES_1G | -0.012 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -2.904 | 242
GRHAMSES_2G | -0.012 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -4.428 | 369
OKLAUN1G | -0.01 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
OKLA7A | -0.01 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.5 | 50
SLSTR1PP_1G | -0.01 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | -0.06 | 6
SWETWATR_4G | -0.009 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | -0.549 | 61
WILDHRS11A | -0.009 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | -0.1134 | 12.6
SWETWATR_3G | -0.009 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | -0.612 | 68
MESQUITW_2G | -0.009 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | -0.2124 | 23.6
SWETWATR_1G | -0.009 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | -0.27 | 30
SWETWATR_2G | -0.009 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | -0.648 | 72
MESQUITW_1G | -0.009 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | -0.36 | 40
ROSCOEWI_5 | -0.008 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | -0.1008 | 12.6
L_SWEETW1_3N | -0.008 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | -0.1424 | 17.8
L_SWEETW1_1N | -0.008 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | -0.1288 | 16.1
L_SWEETW1_2N | -0.008 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | -0.1624 | 20.3
ROSCOEW_5 | -0.008 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | -0.1672 | 20.9
CIELOGEN_1G | -0.008 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | -0.0792 | 9.9
L_BITTCR1_1N | -0.008 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | -0.0448 | 5.6
L_SWEETW1_4N | -0.008 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | -0.1256 | 15.7
KINDERMG_1G | -0.008 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
RDCNYNG1 | -0.008 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | -0.0672 | 8.4
SCURRYCW_1G | -0.008 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | -0.1128 | 14.1
CIELOGEN_2G | -0.008 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | -0.0488 | 6.1
WHRLWIND1A | -0.008 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | -0.048 | 6
KINDERMG_3G | -0.008 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
KINDERMG_2G | -0.008 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
L_DELAWA1_1Y | -0.007 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | -0.0364 | 5.2
MRGNEG_5G | -0.007 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | -0.476 | 68
MCDDONAL_8 | -0.007 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | -0.1498 | 21.4
BSP_1 | -0.007 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
PBCTCGE_3G | -0.007 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | -0.434 | 62
TIEHVSG_2G | -0.007 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.477 | 211
STANTONW_8 | -0.007 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | -0.0707 | 10.1
CALENG2G_2G | -0.007 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | -0.518 | 74
CALENG1G_1G | -0.007 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | -0.511 | 73
MRGNFG_6G | -0.007 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | -0.462 | 66
SNYDERW1A | -0.007 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | -0.0441 | 6.3
MRGNDG_4G | -0.007 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.49 | 70
OCOTILLO_1G | -0.007 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | -0.0406 | 5.8
ATKINS5 | -0.007 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0
ATKINS7 | -0.007 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0
ATKINS4 | -0.007 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0
ATKINS6 | -0.007 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0
MRGNCG_3G | -0.007 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.49 | 70
ATKINS3 | -0.007 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0
TAMUGEN1 | -0.007 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | -0.224 | 32
MRGNBG_2G | -0.007 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | -0.497 | 71
NAV4CT | -0.007 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.56 | 80
GIBN_CREK_G1 | -0.007 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
TRENTIPP_8 | -0.007 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | -0.1575 | 22.5
MRGNAG_1G | -0.007 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | -0.483 | 69
MORGAN5G_5G | -0.007 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | -0.959 | 137
L_DELAWA1_1Y | -0.007 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | -0.0315 | 4.5
PB6GEN_7G | -0.007 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | -3.605 | 515
TIEHVCG_4G | -0.007 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | -1.043 | 149
TIEHVCG_3G | -0.007 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -0.924 | 132
PBCTAGE_1G | -0.007 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | -0.448 | 64
TIEHVSG_1G | -0.007 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.477 | 211
NAV6ST | -0.007 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.805 | 115
PB5GEN_6G | -0.007 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | -0.805 | 115
NAV3ST | -0.007 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.805 | 115
NAV2CT | -0.007 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.56 | 80
NAV1CT | -0.007 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.56 | 80
PBCTEGE_5G | -0.007 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | -0.455 | 65
PBCTDGE_4G | -0.007 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | -0.455 | 65
AEPWIND_8 | -0.007 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | -0.1064 | 15.2
LONGSHORT_5 | -0.007 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | -0.105 | 15
TIEHVCG_2G | -0.007 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -0.924 | 132
PBCTBGE_2G | -0.007 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | -0.455 | 65
TIEHVCG_1G | -0.007 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | -1.015 | 145
AIRTRICITY_8 | -0.007 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | -0.126 | 18
NAV5CT | -0.007 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.56 | 80
CALENG3G_3G | -0.007 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | -0.483 | 69
LOUIS1A | -0.006 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | -0.153 | 25.5
DANSBY14 | -0.006 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | -0.486 | 81
DANSBY2 | -0.006 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | -0.276 | 46
L_DIVIDE1_1N | -0.006 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | -0.159 | 26.5
CIRELLO | -0.006 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | -0.21 | 35
NWPWRG1_1G | -0.006 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | -0.0204 | 3.4
HORSH3 | -0.006 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | -0.2016 | 33.6
HORSH1 | -0.006 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | -0.1998 | 33.3
L_GASCCR1_1N | -0.006 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | -0.09 | 15
HORSH4 | -0.006 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | -0.1032 | 17.2
HORSH2 | -0.006 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | -0.1656 | 27.6
BUFGGEN | -0.006 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | -0.108 | 18
WESTXWIN_1G | -0.006 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | -0.0042 | 0.7
FTR_GT2_5110 | -0.005 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | -0.795 | 159
RIO_DRCS | -0.005 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
FTR_GT3_5085 | -0.005 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | -0.79 | 158
FTR_GT1_5105 | -0.005 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | -0.78 | 156
SWMESA | -0.005 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | -0.056 | 11.2
TNWDWRDU2_8 | -0.005 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | -0.06 | 12
KM SWP | -0.005 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.06 | 12
WDWDU1 | -0.005 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | -0.06 | 12
KM NEP | -0.005 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.06 | 12
FTR_CN4_5095 | -0.005 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | -1.9 | 380
CALHN_G1 | -0.005 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | -0.0855 | 17.1
KM NWP | -0.005 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.06 | 12
KM SEP | -0.005 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | -0.03 | 6
DSKY1 | -0.004 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | -0.0504 | 12.6
ORNNWP1 | -0.004 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | -0.048 | 12
DSKY2 | -0.004 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | -0.046 | 11.5
FRNDDRCS | -0.001 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
CVC_GT1_5035 | 0.001 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | 0.155 | 155
CVC_GT3_5045 | 0.001 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | 0.158 | 158
CHE_GT2_5030 | 0.001 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | 0.173 | 173
CVC_GT2_5020 | 0.001 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | 0.159 | 159
CVC_ST5_5040 | 0.001 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | 0.133 | 133
PSA_GT1_8160 | 0.002 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | 0.13 | 65
EXN_GT | 0.002 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | 0.162 | 81
EXN944GT | 0.002 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | 0.066 | 33
EXN943GT | 0.002 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.038 | 19
EXN942GT | 0.002 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | 0.04 | 20
EXN938GT | 0.002 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | 0.086 | 43
EXN_14GT | 0.002 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | 0.28 | 140
THW_5556 | 0.002 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0328 | 16.4
EXN_17GT | 0.002 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | 0.062 | 31
THW_5354 | 0.002 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0.0332 | 16.6
THW_5354 | 0.002 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0328 | 16.4
THW_5152 | 0.002 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
THW_GT1_GT_1 | 0.002 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
THW_4344 | 0.002 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.116 | 58
THW_4344 | 0.002 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.116 | 58
THW_4142 | 0.002 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.116 | 58
THW_3334 | 0.002 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.116 | 58
THW_3334 | 0.002 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | 0.116 | 58
THW_3132 | 0.002 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.114 | 57
THW_ST4_ST_4 | 0.002 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | 0.216 | 108
THW_ST3_ST_3 | 0.002 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | 0.22 | 110
SRB_GN3_3 | 0.002 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | 0.44 | 220
SOL_GT1 | 0.002 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | 0.0324 | 16.2
SHELLG3_3020 | 0.002 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | 0.06 | 30
SHELLG3_3020 | 0.002 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | 0.078 | 39
SHELLG2 | 0.002 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | 0.144 | 72
SHELLG1_3015 | 0.002 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | 0.142 | 71
CVC_GT4_8005 | 0.002 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | 0.33 | 165
PSA_GT6_8135 | 0.002 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | 0.118 | 59
PSA_GN1_8165 | 0.002 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | 0.208 | 104
PSA_GT4_8145 | 0.002 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0.132 | 66
PSA_GT3_8150 | 0.002 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | 0.14 | 70
PSA_GT2_8155 | 0.002 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | 0.132 | 66
PSG_GT3_8060 | 0.002 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.328 | 164
PSG_GN2_8050 | 0.002 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | 0.356 | 178
DIB_GT1_8080 | 0.002 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | 0.128 | 64
BTE_GT2_8075 | 0.002 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0.326 | 163
GBY_GN5_5 | 0.002 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | 0.597 | 298.5
EP_1_2 | 0.002 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | 0.042 | 21
EP_1_2 | 0.002 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | 0.01 | 5
DIB_GT3_8090 | 0.002 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | 0.1544 | 77.2
DIB_GT2_8075 | 0.002 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.13 | 65
EXN945GT | 0.002 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | 0.038 | 19
BTE_ST1_8070 | 0.002 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | 0.468 | 234
BTE_GT4_8055 | 0.002 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | 0.326 | 163
BTE_GT3_8045 | 0.002 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | 0.316 | 158
EXN941GT | 0.002 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0.038 | 19
CHE_GN4_8025 | 0.002 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | 0.284 | 142
CHE_GT1_8015 | 0.002 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | 0.346 | 173
CBY_GN1_1 | 0.002 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | 1.496 | 748
LPE_GT2_8075 | 0.002 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.084 | 42
CAL_ST1_8000 | 0.002 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0.13 | 65
CAL_GT1_8045 | 0.002 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | 0.304 | 152
LPE_GT4_8085 | 0.002 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.082 | 41
LPE_GT3_8080 | 0.002 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0.082 | 41
LPE_GT1_8070 | 0.002 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0.084 | 42
APD_GT1_8005 | 0.002 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | 0.28 | 140
PSA_GT5_8140 | 0.002 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | 0.128 | 64
EXN_16GT | 0.002 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | 0.064 | 32
DIB_ST1_8085 | 0.002 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | 0.138 | 69
PSG_GT2_8040 | 0.002 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0.328 | 164
SRB_GN4_4 | 0.002 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | 0.452 | 226
THW_3132 | 0.002 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.114 | 57
THW_4142 | 0.002 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | 0.114 | 57
THW_5152 | 0.002 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | 0.0328 | 16.4
THW_5556 | 0.002 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | 0.0332 | 16.6
CBY_GN2_2 | 0.002 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | 1.502 | 751
EXN_15GT | 0.002 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | 0.066 | 33
DPEC_ST55065 | 0.003 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | 0.846 | 282
SRB_GT211035 | 0.003 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
SRB_GT211035 | 0.003 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
SRB_GN2_2 | 0.003 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | 0.522 | 174
SRB_GN1_1 | 0.003 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | 0.528 | 176
SJS_GT2_GT2 | 0.003 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | 0.147 | 49
SJS_GT1_GT1 | 0.003 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | 0.147 | 49
PHR_GN2_2 | 0.003 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
PR_GT1__9040 | 0.003 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | 0.105 | 35
GBY_83841065 | 0.003 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | 0.06 | 20
GBY_83841065 | 0.003 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | 0.06 | 20
GBY_81821075 | 0.003 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | 0.06 | 20
GBY_81821075 | 0.003 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.144 | 48
GBY_73741085 | 0.003 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | 0.141 | 47
GBY_73741085 | 0.003 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0.144 | 48
DPEC_GT45070 | 0.003 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | 0.474 | 158
DPEC_GT35010 | 0.003 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | 0.48 | 160
DPEC_GT25025 | 0.003 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | 0.468 | 156
DPEC_GT15040 | 0.003 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | 0.486 | 162
CTL_GN2_8155 | 0.003 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | 0.033 | 11
CTL_GN1_8145 | 0.003 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | 0.165 | 55
CTL_GT3_8135 | 0.003 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | 0.273 | 91
CTL_GT2_8130 | 0.003 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | 0.309 | 103
BYU_GT4_8065 | 0.003 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.195 | 65
BYU_GT3_8060 | 0.003 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | 0.201 | 67
BYU_GT2_8055 | 0.003 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | 0.186 | 62
BYU_GT1_8075 | 0.003 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0.195 | 65
CTL_GT4_8140 | 0.003 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | 0.282 | 94
TNSLCGN1__8 | 0.004 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | 0.12 | 30
TNTXCTY1CG8 | 0.004 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | 0.42 | 105
TNDOWCGNGG8 | 0.004 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | 0.12 | 30
TNDOWCGNSG8 | 0.004 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | 0.128 | 32
TNTXCTY4CG8 | 0.004 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | 0.412 | 103
TNTXCTY3CG8 | 0.004 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | 0.34 | 85
TNTXCTY2CG8 | 0.004 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | 0.408 | 102
TNBP_CGN4_8 | 0.004 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | 0.16 | 40
TNBPAMCG4_8 | 0.004 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | 0.384 | 96
TNBPAMCG3_8 | 0.004 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | 0.608 | 152
TNBPAMCG2_8 | 0.004 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | 0.6 | 150
TNBPAMCG1_8 | 0.004 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | 0.62 | 155
TNBP_CGN3_8 | 0.004 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | 0.212 | 53
TNBP_CGN2_8 | 0.004 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | 0.264 | 66
TNBP_CGN1_8 | 0.004 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | 0.24 | 60
WAPGT21_GT1 | 0.005 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
WAP_GN8_8 | 0.005 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
WAP_GN7_7 | 0.005 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN5_5 | 0.005 | 48925 | 5 | HOUSTON | YES | 219.7 | 278 | 657 | 0 | 1 | 0 | 0 | 0
WAP_GN4_4 | 0.005 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | 2.72 | 544
WAP_GN3_3 | 0.005 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | 1.13 | 226
WAP_GN2_2 | 0.005 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | 0.611 | 122.2
WAP_GN1_1 | 0.005 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | 0.6225 | 124.5
MNS_GT | 0.005 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | 0.2305 | 46.1
BVE_ST1_GN1 | 0.005 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | 1.23 | 246
BVE_GT2_5035 | 0.005 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | 0.85 | 170
BVE_GT1_GT1 | 0.005 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | 0.86 | 172
AK_GT1__8040 | 0.005 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | 0.17 | 34
WAP_GN6_6 | 0.005 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
TNSCLP3___8 | 0.006 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | 0.666 | 111
TNSCLP4___8 | 0.006 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | 0.69 | 115
TNSCLP2___8 | 0.006 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | 0.702 | 117
TNSCLP1___8 | 0.006 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | 0.696 | 116
DOW41000 | 0.007 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW39100 | 0.007 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
DOW38200 | 0.007 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW17000 | 0.007 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
DOW38100 | 0.007 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
DOW39200 | 0.007 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
DOW38300 | 0.007 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
BSF_GT1_8070 | 0.007 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | 0.07 | 10
BSF_GT1_8070 | 0.007 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | 0.504 | 72
DOW49000 | 0.007 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
DOW61000 | 0.007 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
DOW63000 | 0.007 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
DOW65000 | 0.007 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
DOW82000 | 0.007 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW84000 | 0.007 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
DOW83000 | 0.007 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW42000 | 0.007 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
DOW81000 | 0.007 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
DOW67000 | 0.007 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW66000 | 0.007 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
DOW64000 | 0.007 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
DOW62000 | 0.007 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
TGF_GT1_8000 | 0.009 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | 0.6228 | 69.2
CBE_ST34 | 0.01 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 1.035 | 103.5
CBE_GT4 | 0.01 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.86 | 86
CBE_GT3 | 0.01 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.86 | 86
CBE_ST12 | 0.01 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 1.035 | 103.5
CBE_GT2 | 0.01 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.86 | 86
CBE_GT1 | 0.01 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0.86 | 86
STP_GN2___2 | 0.01 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
STP_GN1___1 | 0.01 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
AMISTADHDRO2 | 0.014 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | 0.182 | 13
AMISTADHDRO1 | 0.014 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | 0.231 | 16.5
HAMILTON | 0.014 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
SANDOW_4G | 0.015 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 |  | 1.029 | 0 | 0 | 0
FOR_5 | 0.016 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | 1.08 | 67.5
FOR_4 | 0.016 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | 1.1936 | 74.6
FOR_3 | 0.016 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | 1.0528 | 65.8
FOR_2 | 0.016 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | 1.0528 | 65.8
FOR_1 | 0.016 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | 0.9024 | 56.4
ALCOA_G | 0.016 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
FOR_9 | 0.016 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | 0.512 | 32
EPLVT1 | 0.016 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
FOR_10 | 0.016 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | 1.168 | 73
FOR_8 | 0.016 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | 0.448 | 28
ELPS | 0.016 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | 0.096 | 6
FOR_7 | 0.016 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | 0.736 | 46
FOR_6 | 0.016 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | 0.416 | 26
UCAR_1 | 0.017 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | 0.119 | 7
UCAR_2 | 0.017 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | 0.357 | 21
CSDR56 | 0.017 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.663 | 39
VISTRONG2 | 0.017 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
VISTRONG1 | 0.017 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
CSDR11 | 0.017 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | 0.663 | 39
RAYBURNGEN2 | 0.017 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN1 | 0.017 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN3 | 0.017 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0.1054 | 6.2
CSDR7 | 0.017 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | 0.119 | 7
CSDR56 | 0.017 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.255 | 15
AIRCO_G | 0.017 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
CSDR89 | 0.017 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0.255 | 15
CSDR89 | 0.017 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0.663 | 39
DUP1V_1 | 0.018 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | 1.314 | 73
FALCONHYDRO1 | 0.018 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.054 | 3
FALFURRI | 0.018 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
ZAPATA | 0.018 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
SI_RAY10 | 0.018 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 0.846 | 47
SI_RAY5 | 0.018 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0.18 | 10
SI_RAY6 | 0.018 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0.342 | 19
SI_RAY9 | 0.018 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 0.684 | 38
FALCONHYDRO3 | 0.018 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | 0.0504 | 2.8
FALCONHYDRO2 | 0.018 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.054 | 3
RAYBURNCC8 | 0.018 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.9 | 50
RAYBURNCC7 | 0.018 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 0.882 | 49
RAYBURNCC10 | 0.018 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 0.72 | 40
RAYBURNCC9 | 0.018 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0.9 | 50
HECN3 | 0.018 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 3.042 | 169
HECN2 | 0.018 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 2.664 | 148
HECN1 | 0.018 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 2.664 | 148
MVGN#3 | 0.018 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 4.626 | 257
MVGN#2 | 0.018 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 3.69 | 205
MVGN#1 | 0.018 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 3.78 | 210
SLURR | 0.018 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
FGNTS201 | 0.018 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 3.096 | 172
FGNTS101 | 0.018 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 2.628 | 146
FGNTS001 | 0.018 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 2.556 | 142
ICPGN#3 | 0.018 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 2.286 | 127
REYSHR_G | 0.018 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
ICPGN#2 | 0.018 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 2.7 | 150
ICPGN#1 | 0.018 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 2.682 | 149
LGEGN#3 | 0.018 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 1.638 | 91
LGEGN#2 | 0.018 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 2.754 | 153
LGEGN#1 | 0.018 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 2.844 | 158
CNOPST1 | 0.018 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 2.754 | 153
MILHWYS | 0.018 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
CNOPGT2 | 0.018 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 2.97 | 165
CNOPGT1 | 0.018 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 2.952 | 164
CEL_B_1 | 0.018 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 0.522 | 29
STARCO_1 | 0.018 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 0.684 | 38
VAL_2 | 0.018 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.45 | 25
VAL_1 | 0.018 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.45 | 25
KOCHREF2 | 0.018 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 0.684 | 38
DAV_2 | 0.018 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 6.12 | 340
DAV_1 | 0.018 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 6.102 | 339
COSW_2 | 0.018 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0.252 | 14
COSW_1 | 0.018 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0.36 | 20
BEEVILLE | 0.019 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
CIDINDUS | 0.019 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
LAR | 0.019 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
LAR_3 | 0.019 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | 1.4972 | 78.8
LAR_2 | 0.019 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | 0.171 | 9
LAR_1 | 0.019 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | 0.304 | 16
CLO_1 | 0.019 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
L_FPPYD21_3Y | 0.021 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_2Y | 0.021 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_1Y | 0.021 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0
SANMIGUELGEN | 0.021 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
PEARSALLGEN3 | 0.021 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | 0.1302 | 6.2
PEARSALLGEN2 | 0.021 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.1302 | 6.2
PEARSALLGEN1 | 0.021 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.1302 | 6.2
L_LOSTPI1_3Y | 0.022 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | 3.8258 | 173.9
L_LOSTPI1_2Y | 0.022 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | 3.4694 | 157.7
L_LOSTPI1_1Y | 0.022 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | 3.4914 | 158.7
CUECPL2A | 0.022 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | 0.264 | 12
L_RIONOG1S1Y | 0.023 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | 6.739 | 293
L_RIONOG1G3Y | 0.023 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | 3.45 | 150
L_RIONOG1G2Y | 0.023 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | 3.404 | 148
L_RIONOG1G1Y | 0.023 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | 3.381 | 147
L_GUADGE1_6Y | 0.023 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | 4.692 | 204
L_GUADGE1_5Y | 0.023 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | 4.209 | 183
L_GUADGE1_4Y | 0.023 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | 3.427 | 149
L_GUADGE1_3Y | 0.023 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | 3.358 | 146
L_GUADGE1_2Y | 0.023 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | 3.197 | 139
L_GUADGE1_1Y | 0.023 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | 3.473 | 151
AVR1_CT2 | 0.023 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | 3.335 | 145
AVR1_ST1 | 0.023 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | 3.772 | 164
AVR1_CT1 | 0.023 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | 3.45 | 150
WBT4 | 0.023 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | 3.473 | 151
WBT3 | 0.023 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | 2.208 | 96
WBT2 | 0.023 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | 1.84 | 80
WBT1 | 0.023 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | 0.5865 | 25.5
JKS1 | 0.023 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
OWS2 | 0.023 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | 8.717 | 379
OWS1 | 0.023 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | 9.591 | 417
LCPCT4 | 0.023 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 1.035 | 45
LCPCT3 | 0.023 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | 1.012 | 44
LCPCT2 | 0.023 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | 1.058 | 46
LCPCT1 | 0.023 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 1.035 | 45
LCP4 | 0.023 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | 2.185 | 95
LCP3 | 0.023 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | 1.334 | 58
JTD2 | 0.023 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
JTD1 | 0.023 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
VHB3 | 0.023 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | 9.131 | 397
VHB2 | 0.023 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | 5.06 | 220
VHB1 | 0.023 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | 4.738 | 206
L_BASTEN1_3Y | 0.024 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | 5.448 | 227
L_BASTEN1_2Y | 0.024 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | 3.504 | 146
L_BASTEN1_1Y | 0.024 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | 3.528 | 147
L_LAKEWO9_1Y | 0.024 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_LAKEWO9_1Y | 0.024 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_SCHUMA8_1Y | 0.024 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.024 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.024 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.024 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_HAYSEN1_4Y | 0.024 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | 5.496 | 229
L_HAYSEN1_3Y | 0.024 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | 5.424 | 226
L_HAYSEN1_2Y | 0.024 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | 5.376 | 224
L_HAYSEN1_1Y | 0.024 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | 5.352 | 223
L_SIMGID1_3Y | 0.025 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | 8.1225 | 324.9
L_SIMGID1_2Y | 0.025 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | 3.325 | 133
L_SIMGID1_1Y | 0.025 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | 3.325 | 133
L_CANYHY8_1Y | 0.028 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0
SANDHG5C | 0.029 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | 4.06 | 140
SANDHG5A | 0.029 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | 4.35 | 150
SANDH_G4 | 0.029 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 1.305 | 45
SANDH_G3 | 0.029 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | 1.305 | 45
SANDH_G2 | 0.029 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 1.305 | 45
SANDH_G1 | 0.029 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | 1.305 | 45
DECKR_G6 | 0.029 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | 1.276 | 44
DECKR_G5 | 0.029 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 1.276 | 44
DECKR_G4 | 0.029 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 1.276 | 44
DECKR_G3 | 0.029 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0
DECKR_G2 | 0.029 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | 11.6 | 400
DECKR_G1 | 0.029 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | 9.28 | 320
L_AUSTPL1_1Y | 0.031 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.217 | 7
L_AUSTPL1_1Y | 0.031 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.217 | 7
L_MARSFO1G3Y | 0.047 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 1.034 | 22
L_MARSFO1G2Y | 0.047 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | 0.752 | 16
L_MARSFO1G1Y | 0.047 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 1.034 | 22
L_MARBFA1_2Y | 0.077 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | 1.001 | 13
L_MARBFA1_1Y | 0.077 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_FERGUS1_1Y | 0.091 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | 36.309 | 399
L_WIRTZ_1G2Y | 0.092 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | 1.656 | 18
L_WIRTZ_1G1Y | 0.092 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
L_INKSDA1_1Y | 0.119 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | 1.19 | 10
L_BUCHAN1_3Y | 0.131 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | 1.441 | 11
L_BUCHAN1_2Y | 0.131 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_1Y | 0.131 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | 1.834 | 14

## 5
Generator Sensitivities |  |  | -1
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
SANDOW_4G | 0.321 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 |  | 1.029 | 0 | 0 | 0 |  | Sum GSF*Pgen
DANSBY2 | 0.03 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | 1.38 | 46 | HOUSTON | -13.2051
DANSBY14 | 0.03 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | 2.43 | 81 | NORTH | -190.5598
ATKINS5 | 0.025 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0 | SOUTH | 30.8889
ATKINS6 | 0.025 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0 | WEST | -45.5273
L_SIMGID1_1Y | 0.025 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | 3.325 | 133
L_SIMGID1_3Y | 0.025 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | 8.1225 | 324.9 |  | Sum Pgen
ATKINS7 | 0.025 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0 | HOUSTON | 13825.3
ATKINS3 | 0.025 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0 | NORTH | 19200.9
L_SIMGID1_2Y | 0.025 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | 3.325 | 133 | SOUTH | 13890.7
ATKINS4 | 0.025 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0 | WEST | 4928.9
TAMUGEN1 | 0.022 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | 0.704 | 32
L_AUSTPL1_1Y | 0.02 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.14 | 7
L_AUSTPL1_1Y | 0.02 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | 0.14 | 7 |  | AWGSF
DECKR_G4 | 0.019 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.836 | 44 | HOUSTON | -0.00095514
L_MARSFO1G3Y | 0.019 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.418 | 22 | NORTH | -0.0099245
DECKR_G6 | 0.019 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | 0.836 | 44 | SOUTH | 0.0022237
L_MARSFO1G2Y | 0.019 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | 0.304 | 16 | WEST | -0.0092368
DECKR_G3 | 0.019 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0
DECKR_G5 | 0.019 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | 0.836 | 44
L_MARSFO1G1Y | 0.019 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | 0.418 | 22 | N to H | -0.0089694
DECKR_G1 | 0.018 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | 5.76 | 320 | N to S | -0.012148
DECKR_G2 | 0.018 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | 7.2 | 400 | W to N | 0.00068772
SANDHG5A | 0.015 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | 2.25 | 150
SANDH_G4 | 0.015 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.675 | 45
SANDH_G2 | 0.015 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | 0.675 | 45
SANDHG5C | 0.015 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | 2.1 | 140
SANDH_G3 | 0.015 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | 0.675 | 45
SANDH_G1 | 0.015 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | 0.675 | 45
L_MARBFA1_1Y | 0.014 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_MARBFA1_2Y | 0.014 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | 0.182 | 13
L_WIRTZ_1G1Y | 0.012 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
L_WIRTZ_1G2Y | 0.012 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | 0.216 | 18
L_BUCHAN1_2Y | 0.011 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_3Y | 0.011 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | 0.121 | 11
L_FERGUS1_1Y | 0.011 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | 4.389 | 399
L_BUCHAN1_1Y | 0.011 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | 0.154 | 14
L_INKSDA1_1Y | 0.01 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | 0.1 | 10
L_LAKEWO9_1Y | 0.005 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
L_CANYHY8_1Y | 0.005 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0
L_LAKEWO9_1Y | 0.005 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0
CUECPL2A | 0.004 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | 0.048 | 12
GIBN_CREK_G1 | 0.003 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
FTR_GT1_5105 | 0.002 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | 0.312 | 156
FTR_GT2_5110 | 0.002 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | 0.318 | 159
L_MCQUEE9_1Y | 0.002 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0.002 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
FTR_GT3_5085 | 0.002 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | 0.316 | 158
L_MCQUEE9_1Y | 0.002 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
FTR_CN4_5095 | 0.002 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | 0.76 | 380
SLURR | 0 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
SI_RAY5 | 0 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0 | 10
FGNTS201 | 0 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 0 | 172
TGF_GT1_8000 | 0 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | 0 | 69.2
ICPGN#2 | 0 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 0 | 150
FOR_4 | 0 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | 0 | 74.6
CSDR56 | 0 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0 | 39
CSDR56 | 0 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0 | 15
FOR_9 | 0 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | 0 | 32
UCAR_1 | 0 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | 0 | 7
RAYBURNCC9 | 0 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0 | 50
CBE_GT4 | 0 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0 | 86
FOR_6 | 0 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | 0 | 26
MVGN#1 | 0 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 0 | 210
HECN2 | 0 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 0 | 148
ICPGN#3 | 0 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 0 | 127
RAYBURNGEN3 | 0 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0 | 6.2
BEEVILLE | 0 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
CBE_ST34 | 0 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0 | 103.5
VISTRONG2 | 0 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
CBE_GT2 | 0 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0 | 86
MVGN#2 | 0 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 0 | 205
FOR_5 | 0 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | 0 | 67.5
VAL_2 | 0 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0 | 25
AIRCO_G | 0 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
RAYBURNCC10 | 0 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 0 | 40
CNOPGT1 | 0 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 0 | 164
RAYBURNGEN1 | 0 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
LGEGN#2 | 0 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 0 | 153
DAV_2 | 0 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 0 | 340
L_SCHUMA8_1Y | 0 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
SI_RAY10 | 0 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 0 | 47
FGNTS101 | 0 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 0 | 146
CSDR11 | 0 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | 0 | 39
FOR_2 | 0 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | 0 | 65.8
LGEGN#3 | 0 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 0 | 91
FOR_7 | 0 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | 0 | 46
RAYBURNGEN2 | 0 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
VAL_1 | 0 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0 | 25
CNOPST1 | 0 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 0 | 153
UCAR_2 | 0 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | 0 | 21
RAYBURNCC7 | 0 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 0 | 49
VISTRONG1 | 0 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
CSDR7 | 0 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | 0 | 7
FOR_8 | 0 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | 0 | 28
MILHWYS | 0 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
FOR_10 | 0 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | 0 | 73
MVGN#3 | 0 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 0 | 257
FGNTS001 | 0 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 0 | 142
ICPGN#1 | 0 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 0 | 149
CBE_ST12 | 0 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | 0 | 103.5
COSW_1 | 0 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0 | 20
CBE_GT1 | 0 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0 | 86
CBE_GT3 | 0 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | 0 | 86
CEL_B_1 | 0 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 0 | 29
ALCOA_G | 0 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
LGEGN#1 | 0 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 0 | 158
COSW_2 | 0 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0 | 14
KOCHREF2 | 0 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 0 | 38
CSDR89 | 0 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | 0 | 15
HECN1 | 0 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 0 | 148
SI_RAY6 | 0 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0 | 19
RAYBURNCC8 | 0 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0 | 50
DUP1V_1 | 0 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | 0 | 73
REYSHR_G | 0 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
FOR_3 | 0 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | 0 | 65.8
DAV_1 | 0 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 0 | 339
CNOPGT2 | 0 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 0 | 165
SI_RAY9 | 0 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 0 | 38
CLO_1 | 0 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
FOR_1 | 0 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | 0 | 56.4
STARCO_1 | 0 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 0 | 38
CSDR89 | 0 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | 0 | 39
HECN3 | 0 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 0 | 169
TNBPAMCG4_8 | -0.001 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | -0.096 | 96
EXN945GT | -0.001 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | -0.019 | 19
PSA_GT6_8135 | -0.001 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | -0.059 | 59
DOW41000 | -0.001 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW17000 | -0.001 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
DOW38200 | -0.001 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW39100 | -0.001 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
TNSCLP2___8 | -0.001 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | -0.117 | 117
DIB_GT1_8080 | -0.001 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | -0.064 | 64
THW_4344 | -0.001 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
BVE_GT2_5035 | -0.001 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | -0.17 | 170
WBT1 | -0.001 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | -0.0255 | 25.5
GBY_83841065 | -0.001 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | -0.02 | 20
DOW63000 | -0.001 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
DOW64000 | -0.001 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
LCPCT4 | -0.001 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | -0.045 | 45
TNBP_CGN4_8 | -0.001 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | -0.04 | 40
TNBPAMCG2_8 | -0.001 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | -0.15 | 150
LCPCT2 | -0.001 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | -0.046 | 46
WBT3 | -0.001 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | -0.096 | 96
WBT2 | -0.001 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | -0.08 | 80
WAPGT21_GT1 | -0.001 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
BVE_GT1_GT1 | -0.001 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | -0.172 | 172
L_RIONOG1G2Y | -0.001 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | -0.148 | 148
DOW38100 | -0.001 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
SRB_GN2_2 | -0.001 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | -0.174 | 174
CTL_GT4_8140 | -0.001 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | -0.094 | 94
TNSCLP4___8 | -0.001 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | -0.115 | 115
TNBPAMCG1_8 | -0.001 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | -0.155 | 155
TNTXCTY2CG8 | -0.001 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | -0.102 | 102
EP_1_2 | -0.001 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | -0.021 | 21
L_GUADGE1_5Y | -0.001 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | -0.183 | 183
CVC_ST5_5040 | -0.001 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | -0.133 | 133
LCP3 | -0.001 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | -0.058 | 58
JTD1 | -0.001 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
CIDINDUS | -0.001 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
TNTXCTY3CG8 | -0.001 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | -0.085 | 85
THW_ST3_ST_3 | -0.001 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | -0.11 | 110
VHB1 | -0.001 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | -0.206 | 206
DPEC_GT25025 | -0.001 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | -0.156 | 156
DOW84000 | -0.001 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
GBY_83841065 | -0.001 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | -0.02 | 20
DPEC_GT35010 | -0.001 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | -0.16 | 160
SJS_GT2_GT2 | -0.001 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | -0.049 | 49
ZAPATA | -0.001 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
PSG_GT2_8040 | -0.001 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | -0.164 | 164
TNTXCTY4CG8 | -0.001 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | -0.103 | 103
LAR_2 | -0.001 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | -0.009 | 9
DOW82000 | -0.001 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
CVC_GT1_5035 | -0.001 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | -0.155 | 155
LPE_GT2_8075 | -0.001 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | -0.042 | 42
PSA_GT5_8140 | -0.001 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | -0.064 | 64
VHB2 | -0.001 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | -0.22 | 220
AK_GT1__8040 | -0.001 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | -0.034 | 34
GBY_GN5_5 | -0.001 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | -0.2985 | 298.5
LCPCT1 | -0.001 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | -0.045 | 45
DOW65000 | -0.001 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
THW_5556 | -0.001 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
PSA_GT2_8155 | -0.001 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | -0.066 | 66
PSA_GT1_8160 | -0.001 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | -0.065 | 65
LAR_3 | -0.001 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | -0.0788 | 78.8
DOW83000 | -0.001 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
VHB3 | -0.001 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | -0.397 | 397
CVC_GT4_8005 | -0.001 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | -0.165 | 165
SHELLG2 | -0.001 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | -0.072 | 72
L_GUADGE1_1Y | -0.001 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | -0.151 | 151
L_GUADGE1_2Y | -0.001 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | -0.139 | 139
CVC_GT2_5020 | -0.001 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | -0.159 | 159
FALFURRI | -0.001 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
SRB_GN3_3 | -0.001 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | -0.22 | 220
BSF_GT1_8070 | -0.001 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | -0.01 | 10
DOW39200 | -0.001 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
DOW81000 | -0.001 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
PSG_GT3_8060 | -0.001 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | -0.164 | 164
JTD2 | -0.001 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
L_GUADGE1_3Y | -0.001 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | -0.146 | 146
DOW67000 | -0.001 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW66000 | -0.001 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
GBY_73741085 | -0.001 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | -0.048 | 48
DOW42000 | -0.001 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
DPEC_GT45070 | -0.001 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | -0.158 | 158
EP_1_2 | -0.001 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | -0.005 | 5
OWS2 | -0.001 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | -0.379 | 379
PSG_GN2_8050 | -0.001 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | -0.178 | 178
JKS1 | -0.001 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
OWS1 | -0.001 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | -0.417 | 417
THW_ST4_ST_4 | -0.001 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | -0.108 | 108
DOW62000 | -0.001 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
DPEC_GT15040 | -0.001 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | -0.162 | 162
DPEC_ST55065 | -0.001 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | -0.282 | 282
LCPCT3 | -0.001 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | -0.044 | 44
LAR_1 | -0.001 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | -0.016 | 16
CHE_GT1_8015 | -0.001 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | -0.173 | 173
TNTXCTY1CG8 | -0.001 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | -0.105 | 105
GBY_81821075 | -0.001 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | -0.048 | 48
GBY_73741085 | -0.001 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | -0.047 | 47
EXN944GT | -0.001 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | -0.033 | 33
THW_3132 | -0.001 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
WAP_GN8_8 | -0.001 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
LCP4 | -0.001 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | -0.095 | 95
THW_4142 | -0.001 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_4142 | -0.001 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
TNBP_CGN1_8 | -0.001 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | -0.06 | 60
THW_GT1_GT_1 | -0.001 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
TNSLCGN1__8 | -0.001 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | -0.03 | 30
AVR1_CT2 | -0.001 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | -0.145 | 145
DOW61000 | -0.001 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
THW_5152 | -0.001 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
SHELLG1_3015 | -0.001 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | -0.071 | 71
THW_3132 | -0.001 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
THW_5152 | -0.001 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
SRB_GT211035 | -0.001 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
BYU_GT1_8075 | -0.001 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | -0.065 | 65
DIB_ST1_8085 | -0.001 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | -0.069 | 69
TNDOWCGNGG8 | -0.001 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | -0.03 | 30
TNSCLP3___8 | -0.001 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | -0.111 | 111
DIB_GT3_8090 | -0.001 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | -0.0772 | 77.2
WAP_GN5_5 | -0.001 | 48925 | 5 | HOUSTON | YES | 216.7 | 278 | 657 | 0 | 1 | 0 | 0 | 0
WAP_GN4_4 | -0.001 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | -0.544 | 544
BSF_GT1_8070 | -0.001 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | -0.072 | 72
LPE_GT4_8085 | -0.001 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | -0.041 | 41
SJS_GT1_GT1 | -0.001 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | -0.049 | 49
LPE_GT3_8080 | -0.001 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | -0.041 | 41
L_RIONOG1G1Y | -0.001 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | -0.147 | 147
L_RIONOG1S1Y | -0.001 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | -0.293 | 293
CTL_GN2_8155 | -0.001 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | -0.011 | 11
THW_5556 | -0.001 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | -0.0166 | 16.6
DOW49000 | -0.001 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
CTL_GN1_8145 | -0.001 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | -0.055 | 55
EXN943GT | -0.001 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | -0.019 | 19
CHE_GT2_5030 | -0.001 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | -0.173 | 173
CHE_GN4_8025 | -0.001 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | -0.142 | 142
BTE_GT3_8045 | -0.001 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | -0.158 | 158
EXN938GT | -0.001 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | -0.043 | 43
CAL_ST1_8000 | -0.001 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | -0.065 | 65
BVE_ST1_GN1 | -0.001 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | -0.246 | 246
LPE_GT1_8070 | -0.001 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | -0.042 | 42
APD_GT1_8005 | -0.001 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | -0.14 | 140
WAP_GN7_7 | -0.001 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN2_2 | -0.001 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | -0.1222 | 122.2
DIB_GT2_8075 | -0.001 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | -0.065 | 65
CAL_GT1_8045 | -0.001 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | -0.152 | 152
GBY_81821075 | -0.001 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | -0.02 | 20
BYU_GT4_8065 | -0.001 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | -0.065 | 65
STP_GN1___1 | -0.001 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
SANMIGUELGEN | -0.001 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
EXN_16GT | -0.001 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | -0.032 | 32
TNDOWCGNSG8 | -0.001 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | -0.032 | 32
BTE_GT4_8055 | -0.001 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | -0.163 | 163
DOW38300 | -0.001 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
EXN942GT | -0.001 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | -0.02 | 20
PHR_GN2_2 | -0.001 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
PSA_GT3_8150 | -0.001 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | -0.07 | 70
PSA_GT4_8145 | -0.001 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | -0.066 | 66
PSA_GN1_8165 | -0.001 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | -0.104 | 104
CVC_GT3_5045 | -0.001 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | -0.158 | 158
PEARSALLGEN2 | -0.001 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | -0.0062 | 6.2
AVR1_CT1 | -0.001 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | -0.15 | 150
EXN_15GT | -0.001 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | -0.033 | 33
SHELLG3_3020 | -0.001 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | -0.039 | 39
PR_GT1__9040 | -0.001 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | -0.035 | 35
PEARSALLGEN3 | -0.001 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | -0.0062 | 6.2
AVR1_ST1 | -0.001 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | -0.164 | 164
SHELLG3_3020 | -0.001 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | -0.03 | 30
WAP_GN1_1 | -0.001 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | -0.1245 | 124.5
MNS_GT | -0.001 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | -0.0461 | 46.1
SRB_GN1_1 | -0.001 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | -0.176 | 176
SRB_GN4_4 | -0.001 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | -0.226 | 226
SRB_GT211035 | -0.001 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
STP_GN2___2 | -0.001 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
PEARSALLGEN1 | -0.001 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | -0.0062 | 6.2
EXN941GT | -0.001 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | -0.019 | 19
TNSCLP1___8 | -0.001 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | -0.116 | 116
THW_3334 | -0.001 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
TNBPAMCG3_8 | -0.001 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | -0.152 | 152
THW_3334 | -0.001 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
L_GUADGE1_4Y | -0.001 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | -0.149 | 149
BTE_ST1_8070 | -0.001 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | -0.234 | 234
THW_4344 | -0.001 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
L_GUADGE1_6Y | -0.001 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | -0.204 | 204
FALCONHYDRO3 | -0.001 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | -0.0028 | 2.8
CBY_GN1_1 | -0.001 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | -0.748 | 748
WAP_GN6_6 | -0.001 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
FALCONHYDRO2 | -0.001 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | -0.003 | 3
LAR | -0.001 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
THW_5354 | -0.001 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | -0.0166 | 16.6
EXN_GT | -0.001 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | -0.081 | 81
TNBP_CGN3_8 | -0.001 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | -0.053 | 53
WAP_GN3_3 | -0.001 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | -0.226 | 226
CTL_GT2_8130 | -0.001 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | -0.103 | 103
L_RIONOG1G3Y | -0.001 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | -0.15 | 150
TNBP_CGN2_8 | -0.001 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | -0.066 | 66
EXN_14GT | -0.001 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | -0.14 | 140
BTE_GT2_8075 | -0.001 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | -0.163 | 163
EXN_17GT | -0.001 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | -0.031 | 31
CTL_GT3_8135 | -0.001 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | -0.091 | 91
FALCONHYDRO1 | -0.001 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | -0.003 | 3
BYU_GT2_8055 | -0.001 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | -0.062 | 62
CBY_GN2_2 | -0.001 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | -0.751 | 751
BYU_GT3_8060 | -0.001 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | -0.067 | 67
WBT4 | -0.001 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | -0.151 | 151
THW_5354 | -0.001 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
SOL_GT1 | -0.001 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | -0.0162 | 16.2
L_HAYSEN1_4Y | -0.002 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | -0.458 | 229
L_HAYSEN1_3Y | -0.002 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | -0.452 | 226
L_HAYSEN1_2Y | -0.002 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | -0.448 | 224
L_HAYSEN1_1Y | -0.002 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | -0.446 | 223
EPLVT1 | -0.002 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
ELPS | -0.002 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | -0.012 | 6
HAMILTON | -0.003 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
AMISTADHDRO2 | -0.003 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | -0.039 | 13
L_FPPYD21_3Y | -0.003 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_2Y | -0.003 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0
L_FPPYD11_1Y | -0.003 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0
TNTNPONE_18 | -0.003 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
TNTNPONE_28 | -0.003 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
AMISTADHDRO1 | -0.003 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | -0.0495 | 16.5
LEG_2___2 | -0.005 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
L_BASTEN1_1Y | -0.005 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | -0.735 | 147
LEG_1___1 | -0.005 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
L_BASTEN1_3Y | -0.005 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | -1.135 | 227
L_BASTEN1_2Y | -0.005 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | -0.73 | 146
CALFREST_2G | -0.008 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -1.24 | 155
BBRN_2G | -0.008 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
CHAMPION_1G | -0.008 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
STRYKER_1G | -0.008 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -1.124 | 140.5
L_LOSTPI1_1Y | -0.008 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | -1.2696 | 158.7
CALFREST_6G | -0.008 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -1.408 | 176
FRNDDRCS | -0.008 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
L_LOSTPI1_3Y | -0.008 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | -1.3912 | 173.9
CALFREST_5G | -0.008 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -1.256 | 157
CALFREST_4G | -0.008 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -1.248 | 156
CALFREST_3G | -0.008 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -1.392 | 174
CALFREST_1G | -0.008 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -1.216 | 152
BBRN_1G | -0.008 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
STRYKER_2G | -0.008 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -3.872 | 484
L_LOSTPI1_2Y | -0.008 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | -1.2616 | 157.7
KM NWP | -0.009 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.108 | 12
HORSH3 | -0.009 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | -0.3024 | 33.6
CALHN_G1 | -0.009 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | -0.1539 | 17.1
PBCTDGE_4G | -0.009 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | -0.585 | 65
DSKY2 | -0.009 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | -0.1035 | 11.5
TRINIDAD_6G | -0.009 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -2.034 | 226
FPLEFR1B_G | -0.009 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -1.413 | 157
WDWDU1 | -0.009 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | -0.108 | 12
WESTXWIN_1G | -0.009 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | -0.0063 | 0.7
TRENTIPP_8 | -0.009 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | -0.2025 | 22.5
KM SEP | -0.009 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | -0.054 | 6
RIO_DRCS | -0.009 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
NWPWRG1_1G | -0.009 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | -0.0306 | 3.4
DSKY1 | -0.009 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | -0.1134 | 12.6
LKHB2_G | -0.009 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -4.626 | 514
BUFGGEN | -0.009 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | -0.162 | 18
HORSH2 | -0.009 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | -0.2484 | 27.6
L_DIVIDE1_1N | -0.009 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | -0.2385 | 26.5
FPLEFR2S_G | -0.009 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -3.708 | 412
PBCTBGE_2G | -0.009 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | -0.585 | 65
PBCTCGE_3G | -0.009 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | -0.558 | 62
NAV1CT | -0.009 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.72 | 80
MORGAN5G_5G | -0.009 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | -1.233 | 137
NAV6ST | -0.009 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -1.035 | 115
NAV4CT | -0.009 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.72 | 80
TIEHVSG_2G | -0.009 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.899 | 211
TIEHVCG_1G | -0.009 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | -1.305 | 145
PB6GEN_7G | -0.009 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | -4.635 | 515
TGATEWAY_3G | -0.009 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -1.314 | 146
FPLEFR2B_G | -0.009 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -1.44 | 160
MRGNAG_1G | -0.009 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | -0.621 | 69
TGATEWAY_1G | -0.009 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -1.341 | 149
CALENG2G_2G | -0.009 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | -0.666 | 74
MRGNBG_2G | -0.009 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | -0.639 | 71
SNYDERW1A | -0.009 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | -0.0567 | 6.3
MRGNDG_4G | -0.009 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.63 | 70
SWMESA | -0.009 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | -0.1008 | 11.2
CIELOGEN_1G | -0.009 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | -0.0891 | 9.9
CALENG3G_3G | -0.009 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | -0.621 | 69
L_DELAWA1_1Y | -0.009 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | -0.0468 | 5.2
SCURRYCW_1G | -0.009 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | -0.1269 | 14.1
KINDERMG_1G | -0.009 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
BSP_1 | -0.009 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
AIRTRICITY_8 | -0.009 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | -0.162 | 18
OCOTILLO_1G | -0.009 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | -0.0522 | 5.8
KM NEP | -0.009 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.108 | 12
HORSH1 | -0.009 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | -0.2997 | 33.3
MARTLAKE_2G | -0.009 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
MCDDONAL_8 | -0.009 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | -0.1926 | 21.4
STANTONW_8 | -0.009 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | -0.0909 | 10.1
KINDERMG_3G | -0.009 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
KINDERMG_2G | -0.009 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
L_DELAWA1_1Y | -0.009 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | -0.0405 | 4.5
L_GASCCR1_1N | -0.009 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | -0.135 | 15
CIELOGEN_2G | -0.009 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | -0.0549 | 6.1
LONGSHORT_5 | -0.009 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | -0.135 | 15
HORSH4 | -0.009 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | -0.1548 | 17.2
CALENG1G_1G | -0.009 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | -0.657 | 73
MRGNFG_6G | -0.009 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | -0.594 | 66
MRGNEG_5G | -0.009 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | -0.612 | 68
TNWDWRDU2_8 | -0.009 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | -0.108 | 12
RDCNYNG1 | -0.009 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | -0.0756 | 8.4
MRGNCG_3G | -0.009 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.63 | 70
TGATEWAY_4G | -0.009 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -3.591 | 399
TGATEWAY_2G | -0.009 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -1.152 | 128
MARTLAKE_1G | -0.009 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
FPLEFR2A_G | -0.009 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.53 | 170
FPLEFR1S_G | -0.009 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -3.726 | 414
FPLEFR1C_G | -0.009 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -1.431 | 159
FPLEFR1A_G | -0.009 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.53 | 170
TIEHVCG_4G | -0.009 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | -1.341 | 149
TIEHVCG_2G | -0.009 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.188 | 132
TIEHVSG_1G | -0.009 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -1.899 | 211
NAV5CT | -0.009 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.72 | 80
NAV3ST | -0.009 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -1.035 | 115
NAV2CT | -0.009 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.72 | 80
PB5GEN_6G | -0.009 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | -1.035 | 115
PBCTEGE_5G | -0.009 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | -0.585 | 65
ORNNWP1 | -0.009 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | -0.108 | 12
MARTLAKE_3G | -0.009 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
FPLEFR2C_G | -0.009 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -1.458 | 162
AEPWIND_8 | -0.009 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | -0.1368 | 15.2
CIRELLO | -0.009 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | -0.315 | 35
LOUIS1A | -0.009 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | -0.2295 | 25.5
LKHB1_G | -0.009 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
PBCTAGE_1G | -0.009 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | -0.576 | 64
KM SWP | -0.009 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.108 | 12
TIEHVCG_3G | -0.009 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -1.188 | 132
ENNSTRAC_1G | -0.01 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -1.96 | 196
WFCOGEN_1G | -0.01 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.12 | 12
DENISNDM | -0.01 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.4 | 40
STEAM3 | -0.01 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.41 | 41
L_BITTCR1_1N | -0.01 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | -0.056 | 5.6
OLINGER_G2 | -0.01 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -0.867 | 86.7
SWETWATR_3G | -0.01 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | -0.68 | 68
VALLEY_2G | -0.01 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -5.27 | 527
DENISNDM | -0.01 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.4 | 40
HANDLEY_4G | -0.01 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -2.175 | 217.5
OLINGER_G4 | -0.01 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.591 | 59.1
LAMARPWR_6G | -0.01 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.99 | 199
VALLEY_3G | -0.01 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -1.862 | 186.2
ROSCOEWI_5 | -0.01 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | -0.126 | 12.6
MOSES_2G | -0.01 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
SPENCER_G4 | -0.01 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.48 | 48
JCKCNTY803 | -0.01 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -1.47 | 147
NTHLK1_G | -0.01 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
MRSSHPRD | -0.01 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.12 | 12
L_SWEETW1_4N | -0.01 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | -0.157 | 15.7
WCPWRCO_1G | -0.01 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -2.04 | 204
NTHLK3_G | -0.01 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -2.474 | 247.4
PEC_3G | -0.01 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -0.91 | 91
VALLLEY_1G | -0.01 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -1.4 | 140
NEWMAN_G5 | -0.01 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
OKLAUN1G | -0.01 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
SWETWATR_1G | -0.01 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | -0.3 | 30
OKLA7A | -0.01 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.5 | 50
JCKCNTY801 | -0.01 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -2.88 | 288
NTHTEXAS03 | -0.01 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.15 | 15
WHRLWIND1A | -0.01 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | -0.06 | 6
SWETWATR_2G | -0.01 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | -0.72 | 72
GRHAMSES_1G | -0.01 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -2.42 | 242
L_SWEETW1_3N | -0.01 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | -0.178 | 17.8
WFCOGEN_2G | -0.01 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.12 | 12
SWETWATR_4G | -0.01 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | -0.61 | 61
EAGLEMNT_2G | -0.01 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
LAMARPWR_3G | -0.01 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.99 | 199
KMICHICT5_G | -0.01 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -1.38 | 138
MTCK3_G | -0.01 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
NTHTEXAS01 | -0.01 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.05 | 5
OLINGER_G1 | -0.01 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -0.631 | 63.1
SPENCER_G5 | -0.01 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.52 | 52
PEC_1G | -0.01 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -0.8 | 80
MTCK8_G | -0.01 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -4.77 | 477
WCPWRCO_2G | -0.01 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -2.04 | 204
MESQUITW_1G | -0.01 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | -0.4 | 40
MOSES_3G | -0.01 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0
KMICHIST6_G | -0.01 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -3.03 | 303
PEC_2G | -0.01 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -0.84 | 84
WCPWRCO_3G | -0.01 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -2.42 | 242
WILDHRS11A | -0.01 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | -0.126 | 12.6
SLSTR1PP_1G | -0.01 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | -0.06 | 6
LAMARPWR_1G | -0.01 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -1.54 | 154
STEAM2 | -0.01 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.26 | 26
KMICHICT1_G | -0.01 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -1.42 | 142
EAGLEMNT_3G | -0.01 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
DCEAST | -0.01 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -4.003 | 400.3
MTCK7_G | -0.01 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
MRSSHPRD01 | -0.01 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.12 | 12
MESQUITW_2G | -0.01 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | -0.236 | 23.6
L_SWEETW1_1N | -0.01 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | -0.161 | 16.1
NTHLK2_G | -0.01 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
GRHAMSES_2G | -0.01 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -3.69 | 369
HANDLEY_1G | -0.01 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
EAGLEMNT_1G | -0.01 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
MOSES_1G | -0.01 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
KMICHICT2_G | -0.01 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -1.44 | 144
ENNSTRAC_2G | -0.01 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -1.16 | 116
MTCK6_G | -0.01 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
LAMARPWR_2G | -0.01 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -1.55 | 155
KMICHIST3_G | -0.01 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -3.1 | 310
COLLIN_1G | -0.01 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
MTCK2_G | -0.01 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
WFCOGEN_2G | -0.01 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.12 | 12
NTHTEXAS02 | -0.01 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.05 | 5
LAMARPWR_5G | -0.01 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -1.63 | 163
LAMARPWR_4G | -0.01 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -1.64 | 164
BARTNWND_1G | -0.01 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.12 | 12
WFCOGEN_1G | -0.01 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.12 | 12
ROSCOEW_5 | -0.01 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | -0.209 | 20.9
STEAM1 | -0.01 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
KMICHICT4_G | -0.01 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -1.36 | 136
L_SWEETW1_2N | -0.01 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | -0.203 | 20.3
JCKCNTY802 | -0.01 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -1.47 | 147
OLINGER_G3 | -0.01 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -1.183 | 118.3
HANDLEY_2G | -0.01 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
MDLTHELP_5G | -0.011 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -2.475 | 225
JNSNCNTY802 | -0.011 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -0.99 | 90
RWMILLER02 | -0.011 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -1.309 | 119
DECRDOVA_2G | -0.011 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -0.715 | 65
MDLTHELP_4G | -0.011 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -2.354 | 214
MDLTHELP_6G | -0.011 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -2.519 | 229
RWMILLER04 | -0.011 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -1.122 | 102
HANDLEY_5G | -0.011 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
RWMILLER01 | -0.011 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -0.825 | 75
RWMILLER03 | -0.011 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -1.716 | 156
MDLTHELP_3G | -0.011 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -2.365 | 215
WLFHOLW_1G | -0.011 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -2.376 | 216
DECRDOVA_4G | -0.011 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.715 | 65
COMCHEPK_1G | -0.011 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
DECRDOVA_1G | -0.011 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -8.569 | 779
DECRDOVA_5G | -0.011 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.715 | 65
MDLTHELP_1G | -0.011 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -2.365 | 215
WLFHOLW_3G | -0.011 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -2.948 | 268
COMCHEPK_2G | -0.011 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
MDLTHELP_2G | -0.011 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -2.365 | 215
HANDLEY_3G | -0.011 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -3.8874 | 353.4
JNSNCNTY802 | -0.011 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -1.848 | 168
DECRDOVA_3G | -0.011 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.715 | 65
RWMILLER05 | -0.011 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -1.111 | 101
WLFHOLW_2G | -0.011 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -2.409 | 219
WHITNYDM01 | -0.014 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.21 | 15
WHITNYDM02 | -0.014 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.21 | 15
BOSQUESW803 | -0.015 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -2.16 | 144
BOSQUESW804 | -0.015 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -1.245 | 83
LAKE_CRK2_G | -0.016 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -3.632 | 227
LAKE_CRK1_G | -0.016 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -0.5664 | 35.4
BOSQUESW502 | -0.017 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -2.533 | 149
BOSQUESW501 | -0.017 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -2.567 | 151
THOUSE_1G | -0.019 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -10.697 | 563
THOUSE_2G | -0.019 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -15.295 | 805

## 6
Generator Sensitivities
Name of Bus | P Sensitivity of Bus | Number of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | USE 1 if yes | GSF*PGEn | Use Pgen
L_LAKEWO9_1Y | -0.124 | 7624 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0 |  | Sum GSF*Pgen
L_LAKEWO9_1Y | -0.124 | 7624 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1 | 1 | 0 | 0 | HOUSTON | -3.6601
CUECPL2A | -0.096 | 8189 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.02 | 1 | -1.152 | 12 | NORTH | -115.1502
L_SIMGID1_2Y | -0.037 | 7005 | 2 | SOUTH | YES | 133 | 32 | 139 | 0 | 1.02 | 1 | -4.921 | 133 | SOUTH | 206.8929
L_SIMGID1_3Y | -0.037 | 7006 | 3 | SOUTH | YES | 324.9 | 60 | 331 | 0 | 1.02 | 1 | -12.0213 | 324.9 | WEST | -20.6244
L_SIMGID1_1Y | -0.037 | 7004 | 1 | SOUTH | YES | 133 | 40 | 137 | 0 | 1.02 | 1 | -4.921 | 133
DECKR_G3 | -0.017 | 9002 | 3 | SOUTH | YES | 0 | 24 | 42 |  | 1.015 | 1 | 0 | 0 |  | Sum Pgen
DECKR_G4 | -0.017 | 9003 | 4 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | -0.748 | 44 | HOUSTON | 13825.3
DECKR_G5 | -0.017 | 9004 | 5 | SOUTH | YES | 44 | 24 | 44 | 0 | 1.015 | 1 | -0.748 | 44 | NORTH | 19200.9
DECKR_G6 | -0.017 | 9005 | 6 | SOUTH | YES | 44 | 24 | 47 | 0 | 1.015 | 1 | -0.748 | 44 | SOUTH | 13890.7
SANDHG5C | -0.016 | 9021 | 5C | SOUTH | YES | 140 | 0 | 151 | 0 | 1.0175 | 1 | -2.24 | 140 | WEST | 4928.9
SANDH_G1 | -0.016 | 9016 | 1 | SOUTH | YES | 45 | 2 | 49 | 0 | 1.0175 | 1 | -0.72 | 45
SANDHG5A | -0.016 | 9020 | 5A | SOUTH | YES | 150 | 84 | 159 | 0 | 1.0175 | 1 | -2.4 | 150
SANDH_G4 | -0.016 | 9019 | 4 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | -0.72 | 45 |  | AWGSF
SANDH_G2 | -0.016 | 9017 | 2 | SOUTH | YES | 45 | 2 | 47 | 0 | 1.0175 | 1 | -0.72 | 45 | HOUSTON | -0.00026474
SANDH_G3 | -0.016 | 9018 | 3 | SOUTH | YES | 45 | 2 | 48 | 0 | 1.0175 | 1 | -0.72 | 45 | NORTH | -0.0059971
DECKR_G2 | -0.016 | 9001 | 2 | SOUTH | YES | 400 | 50 | 427 | 0 | 1.015 | 1 | -6.4 | 400 | SOUTH | 0.014894
DECKR_G1 | -0.016 | 9000 | 1 | SOUTH | YES | 320 | 50 | 326 | 0 | 1.015 | 1 | -5.12 | 320 | WEST | -0.0041844
L_LOSTPI1_3Y | -0.015 | 7009 | 3 | SOUTH | YES | 173.9 | 72 | 184 | 0 | 1.015 | 1 | -2.6085 | 173.9
L_BASTEN1_1Y | -0.015 | 7807 | 1 | SOUTH | YES | 147 | 83.5 | 147 | 0 | 1.004 | 1 | -2.205 | 147
L_FPPYD11_1Y | -0.015 | 7010 | 1 | SOUTH | YES | 587.4 | 200 | 605 | 0 | 1.02 | 0 | 0 | 0 | N to H | -0.0057324
L_AUSTPL1_1Y | -0.015 | 7020 | 1 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | -0.105 | 7 | N to S | -0.020891
L_FPPYD11_2Y | -0.015 | 7011 | 2 | SOUTH | YES | 577.4 | 200 | 608 | 0 | 1.02 | 0 | 0 | 0 | W to N | 0.0018127
L_LOSTPI1_1Y | -0.015 | 7007 | 1 | SOUTH | YES | 158.7 | 110 | 167 | 0 | 1.015 | 1 | -2.3805 | 158.7
L_BASTEN1_2Y | -0.015 | 7808 | 1 | SOUTH | YES | 146 | 83.5 | 146 | 0 | 1.004 | 1 | -2.19 | 146
L_BASTEN1_3Y | -0.015 | 7809 | 1 | SOUTH | YES | 227 | 42 | 227 | 0 | 1.004 | 1 | -3.405 | 227
L_AUSTPL1_1Y | -0.015 | 7020 | 2 | SOUTH | YES | 7 | 0 | 8 |  | 1 | 1 | -0.105 | 7
L_FPPYD21_3Y | -0.015 | 7012 | 3 | SOUTH | YES | 427.4 | 200 | 436 | 0 | 1.02 | 0 | 0 | 0
L_LOSTPI1_2Y | -0.015 | 7008 | 2 | SOUTH | YES | 157.7 | 107 | 164 | 0 | 1.015 | 1 | -2.3655 | 157.7
SANDOW_4G | -0.014 | 3432 | 4 | SOUTH | YES | 534 | 460 | 534 | 0 | 1.029 | 0 | 0 | 0
L_MARSFO1G2Y | -0.01 | 7032 | 2 | SOUTH | YES | 16 | 0 | 35 | 0 | 1 | 1 | -0.16 | 16
L_MARSFO1G1Y | -0.01 | 7031 | 1 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | -0.22 | 22
L_MARSFO1G3Y | -0.01 | 7033 | 3 | SOUTH | YES | 22 | 0 | 36 | 0 | 1 | 1 | -0.22 | 22
BOSQUESW502 | -0.008 | 239 | 1 | NORTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | -1.192 | 149
BOSQUESW803 | -0.008 | 251 | 2 | NORTH | YES | 144 | 0 | 144 | 0 | 1.032 | 1 | -1.152 | 144
THOUSE_2G | -0.008 | 3404 | 2 | NORTH | YES | 805 | 250 | 805 | 0 | 1.026 | 1 | -6.44 | 805
BOSQUESW501 | -0.008 | 247 | 2 | NORTH | YES | 151 | 0 | 151 | 0 | 1.03 | 1 | -1.208 | 151
LAKE_CRK1_G | -0.008 | 3416 | 1 | NORTH | YES | 35.4 | 33 | 75 | 0 | 1.043 | 1 | -0.2832 | 35.4
BOSQUESW804 | -0.008 | 253 | 2 | NORTH | YES | 83 | 0 | 83 | 0 | 1.032 | 1 | -0.664 | 83
THOUSE_1G | -0.008 | 3403 | 1 | NORTH | YES | 563 | 200 | 563 | 0 | 1.026 | 1 | -4.504 | 563
LAKE_CRK2_G | -0.008 | 3417 | 2 | NORTH | YES | 227 | 40 | 227 | 0 | 1.029 | 1 | -1.816 | 227
WHITNYDM01 | -0.007 | 244 | 1 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.105 | 15
WHITNYDM02 | -0.007 | 245 | 2 | NORTH | YES | 15 | 0 | 15 | 0 | 1.035 | 1 | -0.105 | 15
MOSES_1G | -0.006 | 1701 | 1 | NORTH | YES | 560 | 175 | 560 | 0 | 1.031 | 0 | 0 | 0
RWMILLER02 | -0.006 | 333 | 2 | NORTH | YES | 119 | 37 | 119 | 0 | 1.04 | 1 | -0.714 | 119
DECRDOVA_1G | -0.006 | 1889 | 1 | NORTH | YES | 779 | 255 | 779 | 0 | 1.022 | 1 | -4.674 | 779
PEC_1G | -0.006 | 1675 | 1 | NORTH | YES | 80 | 35 | 80 | 0 | 1.022 | 1 | -0.48 | 80
PEC_3G | -0.006 | 1677 | 3 | NORTH | YES | 91 | 35 | 91 | 0 | 1.022 | 1 | -0.546 | 91
NTHLK3_G | -0.006 | 2383 | 3 | NORTH | YES | 247.4 | 50 | 329 | 0 | 1.029 | 1 | -1.4844 | 247.4
NTHTEXAS03 | -0.006 | 505 | 3 | NORTH | YES | 15 | 15 | 38 | 0 | 1.015 | 1 | -0.09 | 15
FPLEFR2B_G | -0.006 | 12422 | 2 | NORTH | YES | 160 | 72 | 160 | 0 | 1 | 1 | -0.96 | 160
JNSNCNTY802 | -0.006 | 366 | 1 | NORTH | YES | 168 | 20 | 168 | 0 | 1.02 | 1 | -1.008 | 168
FPLEFR2A_G | -0.006 | 12421 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.02 | 170
FPLEFR1S_G | -0.006 | 12414 | 4 | NORTH | YES | 414 | 191 | 414 | 0 | 1 | 1 | -2.484 | 414
DECRDOVA_2G | -0.006 | 1892 | A | NORTH | YES | 65 | 65 | 71 | 0 | 1.029 | 1 | -0.39 | 65
LAMARPWR_5G | -0.006 | 1682 | 5 | NORTH | YES | 163 | 67.7 | 163 | 0 | 1.031 | 1 | -0.978 | 163
KMICHICT4_G | -0.006 | 11694 | 4 | NORTH | YES | 136 | 80 | 136 | 0 | 1.029 | 1 | -0.816 | 136
RWMILLER03 | -0.006 | 334 | 3 | NORTH | YES | 156 | 65 | 208 | 0 | 1.04 | 1 | -0.936 | 156
MDLTHELP_5G | -0.006 | 1937 | 5 | NORTH | YES | 225 | 74 | 225 | 0 | 1.02 | 1 | -1.35 | 225
LAMARPWR_2G | -0.006 | 1679 | 2 | NORTH | YES | 155 | 67.7 | 155 | 0 | 1.031 | 1 | -0.93 | 155
MDLTHELP_6G | -0.006 | 1938 | 6 | NORTH | YES | 229 | 74 | 229 | 0 | 1.02 | 1 | -1.374 | 229
RWMILLER05 | -0.006 | 336 | 5 | NORTH | YES | 101 | 0 | 101 | 0 | 1.04 | 1 | -0.606 | 101
OLINGER_G2 | -0.006 | 843 | 1 | NORTH | YES | 86.7 | 25 | 105 | 0 | 1.03 | 1 | -0.5202 | 86.7
MOSES_3G | -0.006 | 1703 | 3 | NORTH | YES | 808 | 463 | 808 | 0 | 1.031 | 0 | 0 | 0
EAGLEMNT_3G | -0.006 | 1863 | MB | NORTH | YES | 0 | 50 | 378 |  | 1.033 | 1 | 0 | 0
TGATEWAY_4G | -0.006 | 13119 | 4 | NORTH | YES | 399 | 65 | 399 | 0 | 1.035 | 1 | -2.394 | 399
OLINGER_G3 | -0.006 | 844 | 1 | NORTH | YES | 118.3 | 45 | 148 | 0 | 1.03 | 1 | -0.7098 | 118.3
TGATEWAY_3G | -0.006 | 13118 | 3 | NORTH | YES | 146 | 30 | 146 | 0 | 1.035 | 1 | -0.876 | 146
DENISNDM | -0.006 | 6948 | 2 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.24 | 40
DENISNDM | -0.006 | 6948 | 1 | NORTH | YES | 40 | 5 | 40 | 0 | 1.015 | 1 | -0.24 | 40
OLINGER_G4 | -0.006 | 845 | 1 | NORTH | YES | 59.1 | 0 | 76 | 0 | 1.03 | 1 | -0.3546 | 59.1
VALLEY_3G | -0.006 | 1689 | 3 | NORTH | YES | 186.2 | 25 | 354 | 0 | 1.015 | 1 | -1.1172 | 186.2
WLFHOLW_1G | -0.006 | 1877 | 1 | NORTH | YES | 216 | 89.3 | 216 | 0 | 1.029 | 1 | -1.296 | 216
NEWMAN_G5 | -0.006 | 837 | 1 | NORTH | YES | 0 | 15 | 37 |  | 1.01 | 1 | 0 | 0
COLLIN_1G | -0.006 | 2371 | MB | NORTH | YES | 0 | 40 | 138 |  | 1.022 | 1 | 0 | 0
NTHTEXAS02 | -0.006 | 504 | 2 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.03 | 5
MARTLAKE_1G | -0.006 | 3097 | 1 | NORTH | YES | 799 | 500 | 799 | 0 | 1.031 | 0 | 0 | 0
FPLEFR1C_G | -0.006 | 12413 | 3 | NORTH | YES | 159 | 72 | 159 | 0 | 1 | 1 | -0.954 | 159
DECRDOVA_5G | -0.006 | 1895 | D | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.39 | 65
VALLEY_2G | -0.006 | 1688 | 2 | NORTH | YES | 527 | 90 | 527 | 0 | 1.036 | 1 | -3.162 | 527
KMICHIST6_G | -0.006 | 11696 | 6 | NORTH | YES | 303 | 60 | 303 | 0 | 1.029 | 1 | -1.818 | 303
TGATEWAY_1G | -0.006 | 13116 | 1 | NORTH | YES | 149 | 30 | 149 | 0 | 1.035 | 1 | -0.894 | 149
SPENCER_G5 | -0.006 | 924 | 1 | NORTH | YES | 52 | 20 | 64 | 0 | 1.03 | 1 | -0.312 | 52
MTCK8_G | -0.006 | 2417 | 8 | NORTH | YES | 477 | 60 | 556 | 0 | 1.029 | 1 | -2.862 | 477
STEAM3 | -0.006 | 950 | 1 | NORTH | YES | 41 | 13 | 41 | 0 | 1.02 | 1 | -0.246 | 41
RWMILLER04 | -0.006 | 335 | 4 | NORTH | YES | 102 | 0 | 102 | 0 | 1.04 | 1 | -0.612 | 102
TRINIDAD_6G | -0.006 | 3126 | 1 | NORTH | YES | 226 | 46 | 226 | 0 | 1 | 1 | -1.356 | 226
MTCK7_G | -0.006 | 2414 | 7 | NORTH | YES | 0 | 30 | 114 |  | 1.029 | 1 | 0 | 0
OLINGER_G1 | -0.006 | 842 | 1 | NORTH | YES | 63.1 | 20 | 80 | 0 | 1.03 | 1 | -0.3786 | 63.1
WLFHOLW_2G | -0.006 | 1878 | 2 | NORTH | YES | 219 | 105 | 219 | 0 | 1.029 | 1 | -1.314 | 219
MTCK6_G | -0.006 | 2413 | 6 | NORTH | YES | 0 | 30 | 118 |  | 1.029 | 1 | 0 | 0
SLSTR1PP_1G | -0.006 | 1643 | 1 | NORTH | YES | 6 | 0 | 60 | 0 | 1.022 | 1 | -0.036 | 6
TGATEWAY_2G | -0.006 | 13117 | 2 | NORTH | YES | 128 | 30 | 128 | 0 | 1.035 | 1 | -0.768 | 128
JCKCNTY802 | -0.006 | 581 | 2 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -0.882 | 147
MARTLAKE_3G | -0.006 | 3099 | 3 | NORTH | YES | 804 | 500 | 804 | 0 | 1.031 | 0 | 0 | 0
VALLLEY_1G | -0.006 | 1687 | 1 | NORTH | YES | 140 | 15 | 175 | 0 | 1.036 | 1 | -0.84 | 140
EAGLEMNT_1G | -0.006 | 1861 | MB | NORTH | YES | 0 | 30 | 112 |  | 1.033 | 1 | 0 | 0
MTCK3_G | -0.006 | 2419 | MB | NORTH | YES | 0 | 10 | 63 |  | 0.9667 | 1 | 0 | 0
STRYKER_1G | -0.006 | 3107 | 1 | NORTH | YES | 140.5 | 45 | 182 | 0 | 1.029 | 1 | -0.843 | 140.5
EAGLEMNT_2G | -0.006 | 1862 | MB | NORTH | YES | 0 | 40 | 100 |  | 1.033 | 1 | 0 | 0
KMICHIST3_G | -0.006 | 11693 | 3 | NORTH | YES | 310 | 60 | 310 | 0 | 1.029 | 1 | -1.86 | 310
MOSES_2G | -0.006 | 1702 | 2 | NORTH | YES | 579 | 175 | 579 | 0 | 1.031 | 0 | 0 | 0
ENNSTRAC_1G | -0.006 | 12322 | 1 | NORTH | YES | 196 | 130 | 196 | 0 | 1.043 | 1 | -1.176 | 196
WLFHOLW_3G | -0.006 | 1879 | 3 | NORTH | YES | 268 | 89.3 | 268 | 0 | 1.029 | 1 | -1.608 | 268
KMICHICT2_G | -0.006 | 11692 | 2 | NORTH | YES | 144 | 80 | 144 | 0 | 1.029 | 1 | -0.864 | 144
FPLEFR1A_G | -0.006 | 12411 | 1 | NORTH | YES | 170 | 72 | 170 | 0 | 1 | 1 | -1.02 | 170
LKHB2_G | -0.006 | 2452 | 2 | NORTH | YES | 514 | 80 | 514 | 0 | 1.029 | 1 | -3.084 | 514
HANDLEY_5G | -0.006 | 1949 | 5 | NORTH | YES | 0 | 150 | 435 |  | 1.03 | 1 | 0 | 0
LAMARPWR_4G | -0.006 | 1681 | 4 | NORTH | YES | 164 | 67.7 | 164 | 0 | 1.031 | 1 | -0.984 | 164
FPLEFR2C_G | -0.006 | 12423 | 3 | NORTH | YES | 162 | 72 | 162 | 0 | 1 | 1 | -0.972 | 162
MARTLAKE_2G | -0.006 | 3098 | 2 | NORTH | YES | 795 | 461 | 795 | 0 | 1.031 | 0 | 0 | 0
FPLEFR1B_G | -0.006 | 12412 | 2 | NORTH | YES | 157 | 72 | 157 | 0 | 1 | 1 | -0.942 | 157
LAMARPWR_6G | -0.006 | 1683 | 6 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.194 | 199
NTHLK2_G | -0.006 | 2382 | 2 | NORTH | YES | 0 | 35 | 181 |  | 1.029 | 1 | 0 | 0
DECRDOVA_4G | -0.006 | 1894 | C | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.39 | 65
KMICHICT5_G | -0.006 | 11695 | 5 | NORTH | YES | 138 | 80 | 138 | 0 | 1.029 | 1 | -0.828 | 138
STRYKER_2G | -0.006 | 3108 | 2 | NORTH | YES | 484 | 75 | 484 | 0 | 1.029 | 1 | -2.904 | 484
COMCHEPK_2G | -0.006 | 1899 | 2 | NORTH | YES | 1164 | 1128 | 1164 | 0 | 1.031 | 0 | 0 | 0
DECRDOVA_3G | -0.006 | 1893 | B | NORTH | YES | 65 | 65 | 70 | 0 | 1.029 | 1 | -0.39 | 65
SPENCER_G4 | -0.006 | 923 | 1 | NORTH | YES | 48 | 20 | 61 | 0 | 1.03 | 1 | -0.288 | 48
MDLTHELP_1G | -0.006 | 1941 | 1 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.29 | 215
LAMARPWR_3G | -0.006 | 1680 | 3 | NORTH | YES | 199 | 129.1 | 199 | 0 | 1.031 | 1 | -1.194 | 199
CHAMPION_1G | -0.006 | 3348 | MB | NORTH | YES | 0 | 42 | 42 |  | 1 | 1 | 0 | 0
RWMILLER01 | -0.006 | 332 | 1 | NORTH | YES | 75 | 18.5 | 75 | 0 | 1.04 | 1 | -0.45 | 75
ENNSTRAC_2G | -0.006 | 12323 | 2 | NORTH | YES | 116 | 100 | 116 | 0 | 1.043 | 1 | -0.696 | 116
MTCK2_G | -0.006 | 2418 | 2 | NORTH | YES | 0 | 10 | 23 |  | 0.9667 | 1 | 0 | 0
COMCHEPK_1G | -0.006 | 1898 | 1 | NORTH | YES | 1164 | 1150 | 1164 | 0 | 1.031 | 0 | 0 | 0
LAMARPWR_1G | -0.006 | 1678 | 1 | NORTH | YES | 154 | 67.7 | 154 | 0 | 1.031 | 1 | -0.924 | 154
JNSNCNTY802 | -0.006 | 367 | 2 | NORTH | YES | 90 | 20 | 90 | 0 | 1.02 | 1 | -0.54 | 90
HANDLEY_4G | -0.006 | 1948 | 4 | NORTH | YES | 217.5 | 150 | 435 | 0 | 1.022 | 1 | -1.305 | 217.5
MDLTHELP_3G | -0.006 | 1943 | 3 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.29 | 215
STEAM1 | -0.006 | 948 | 1 | NORTH | YES | 0 | 12 | 20 |  | 1.02 | 1 | 0 | 0
MDLTHELP_2G | -0.006 | 1942 | 2 | NORTH | YES | 215 | 74 | 215 | 0 | 1.02 | 1 | -1.29 | 215
NTHLK1_G | -0.006 | 2381 | 1 | NORTH | YES | 0 | 35 | 156 |  | 1.029 | 1 | 0 | 0
HANDLEY_2G | -0.006 | 1946 | MB | NORTH | YES | 0 | 30 | 68 |  | 1.003 | 1 | 0 | 0
STEAM2 | -0.006 | 949 | 1 | NORTH | YES | 26 | 8 | 26 | 0 | 0.99 | 1 | -0.156 | 26
HANDLEY_1G | -0.006 | 1945 | MB | NORTH | YES | 0 | 25 | 36 |  | 1.003 | 1 | 0 | 0
JCKCNTY801 | -0.006 | 580 | 1 | NORTH | YES | 288 | 0 | 288 | 0 | 1.022 | 1 | -1.728 | 288
JCKCNTY803 | -0.006 | 582 | 3 | NORTH | YES | 147 | 0 | 147 | 0 | 1.022 | 1 | -0.882 | 147
MDLTHELP_4G | -0.006 | 1944 | 4 | NORTH | YES | 214 | 74 | 214 | 0 | 1.02 | 1 | -1.284 | 214
HANDLEY_3G | -0.006 | 1947 | 3 | NORTH | YES | 353.4 | 100 | 392 | 0 | 1.03 | 1 | -2.1204 | 353.4
NTHTEXAS01 | -0.006 | 503 | 1 | NORTH | YES | 5 | 5 | 18 | 0 | 1.015 | 1 | -0.03 | 5
PEC_2G | -0.006 | 1676 | 2 | NORTH | YES | 84 | 35 | 84 | 0 | 1.022 | 1 | -0.504 | 84
LKHB1_G | -0.006 | 2451 | 1 | NORTH | YES | 0 | 80 | 391 |  | 1.029 | 1 | 0 | 0
DCEAST | -0.006 | 5925 | 1 | NORTH | YES | 400.3 | -600 | 600 | 0 | 1.025 | 1 | -2.4018 | 400.3
FPLEFR2S_G | -0.006 | 12424 | 4 | NORTH | YES | 412 | 191 | 412 | 0 | 1 | 1 | -2.472 | 412
KMICHICT1_G | -0.006 | 11691 | 1 | NORTH | YES | 142 | 80 | 142 | 0 | 1.029 | 1 | -0.852 | 142
WCPWRCO_3G | -0.005 | 1455 | 3 | NORTH | YES | 242 | 50 | 242 | 0 | 1.023 | 1 | -1.21 | 242
WCPWRCO_2G | -0.005 | 1454 | 2 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -1.02 | 204
OKLA7A | -0.005 | 6100 | 1 | WEST | YES | 50 | -220 | 220 | 0 | 1.035 | 1 | -0.25 | 50
GRHAMSES_2G | -0.005 | 1432 | 2 | WEST | YES | 369 | 90 | 369 | 0 | 1.023 | 1 | -1.845 | 369
MRSSHPRD | -0.005 | 344 | 1 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.06 | 12
CALFREST_3G | -0.005 | 13133 | 3 | NORTH | YES | 174 | 40 | 174 | 0 | 1.035 | 1 | -0.87 | 174
OKLAUN1G | -0.005 | 6752 | 1 | WEST | YES | 629 | 175 | 629 | 0 | 1.035 | 0 | 0 | 0
SWETWATR_1G | -0.005 | 1416 | 1 | WEST | YES | 30 | 18 | 30 | 0 | 1.039 | 1 | -0.15 | 30
MRSSHPRD01 | -0.005 | 345 | 2 | WEST | YES | 12 | 0 | 12 |  | 1.03 | 1 | -0.06 | 12
SWETWATR_4G | -0.005 | 1419 | 4 | WEST | YES | 61 | 36 | 61 | 0 | 1.039 | 1 | -0.305 | 61
LEG_1___1 | -0.005 | 48721 | 1 | NORTH | YES | 836 | 357 | 836 | 0 | 1.0348 | 0 | 0 | 0
CALFREST_6G | -0.005 | 13136 | 6 | NORTH | YES | 176 | 40 | 176 | 0 | 1.035 | 1 | -0.88 | 176
LEG_2___2 | -0.005 | 48722 | 2 | NORTH | YES | 853 | 357 | 853 | 0 | 1.0348 | 0 | 0 | 0
DANSBY14 | -0.005 | 32892 | 1 | NORTH | YES | 81 | 25 | 108 | 0 | 1.035 | 1 | -0.405 | 81
DANSBY2 | -0.005 | 32884 | 1 | NORTH | YES | 46 | 2 | 46 | 0 | 1.015 | 1 | -0.23 | 46
CALFREST_4G | -0.005 | 13134 | 4 | NORTH | YES | 156 | 40 | 156 | 0 | 1.035 | 1 | -0.78 | 156
CALFREST_2G | -0.005 | 13132 | 2 | NORTH | YES | 155 | 57 | 155 | 0 | 1.035 | 1 | -0.775 | 155
CALFREST_1G | -0.005 | 13131 | 1 | NORTH | YES | 152 | 40 | 152 | 0 | 1.035 | 1 | -0.76 | 152
BARTNWND_1G | -0.005 | 1600 | 1 | WEST | YES | 12 | 0 | 120 | 0 | 1.022 | 1 | -0.06 | 12
SWETWATR_2G | -0.005 | 1417 | 2 | WEST | YES | 72 | 36 | 72 | 0 | 1.039 | 1 | -0.36 | 72
WFCOGEN_2G | -0.005 | 1482 | 2 | WEST | YES | 12 | 12 | 17 | 0 | 1 | 1 | -0.06 | 12
WFCOGEN_2G | -0.005 | 1482 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.06 | 12
CALFREST_5G | -0.005 | 13135 | 5 | NORTH | YES | 157 | 57 | 157 | 0 | 1.035 | 1 | -0.785 | 157
WFCOGEN_1G | -0.005 | 1479 | 2 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.06 | 12
WFCOGEN_1G | -0.005 | 1479 | 1 | WEST | YES | 12 | 12 | 20 | 0 | 1 | 1 | -0.06 | 12
MESQUITW_2G | -0.005 | 1438 | 1 | WEST | YES | 23.6 | 0 | 236 |  | 1.01 | 1 | -0.118 | 23.6
MESQUITW_1G | -0.005 | 1437 | 1 | WEST | YES | 40 | 0 | 400 | 0 | 1.023 | 1 | -0.2 | 40
GRHAMSES_1G | -0.005 | 1433 | 1 | WEST | YES | 242 | 60 | 242 | 0 | 1.038 | 1 | -1.21 | 242
WHRLWIND1A | -0.005 | 60081 | 1 | WEST | YES | 6 | 0 | 60 | 0 | 1.03 | 1 | -0.03 | 6
SWETWATR_3G | -0.005 | 1418 | 3 | WEST | YES | 68 | 36 | 68 | 0 | 1.039 | 1 | -0.34 | 68
WILDHRS11A | -0.005 | 60052 | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0 | 1.005 | 1 | -0.063 | 12.6
BBRN_2G | -0.005 | 3382 | 2 | NORTH | YES | 610 | 225 | 610 | 0 | 1.0345 | 0 | 0 | 0
WCPWRCO_1G | -0.005 | 1453 | 1 | NORTH | YES | 204 | 50 | 204 | 0 | 1.023 | 1 | -1.02 | 204
DUP1V_1 | -0.005 | 8066 | 1 | SOUTH | YES | 73 | 0 | 73 | 0 | 1.0031 | 1 | -0.365 | 73
BBRN_1G | -0.005 | 3381 | 1 | NORTH | YES | 597 | 225 | 597 | 0 | 1.0345 | 0 | 0 | 0
KINDERMG_3G | -0.004 | 1071 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
OCOTILLO_1G | -0.004 | 1328 | 1 | WEST | YES | 5.8 | 0 | 58 |  | 0.99 | 1 | -0.0232 | 5.8
WESTXWIN_1G | -0.004 | 1349 | 1 | WEST | YES | 0.7 | 0 | 6.6 |  | 1.02 | 1 | -0.0028 | 0.7
HORSH3 | -0.004 | 60070 | 1 | WEST | YES | 33.6 | 0 | 224 | 0 | 1.025 | 1 | -0.1344 | 33.6
KINDERMG_1G | -0.004 | 1069 | 1 | WEST | YES | 25 | 5 | 25 | 0 | 1.01 | 0 | 0 | 0
TIEHVSG_2G | -0.004 | 11025 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -0.844 | 211
TIEHVCG_2G | -0.004 | 11022 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -0.528 | 132
HORSH4 | -0.004 | 60072 | 1 | WEST | YES | 17.2 | 0 | 115 | 0 | 1.025 | 1 | -0.0688 | 17.2
MRGNEG_5G | -0.004 | 1043 | E | WEST | YES | 68 | 68 | 68 |  | 0.99 | 1 | -0.272 | 68
SCURRYCW_1G | -0.004 | 1068 | 1 | WEST | YES | 14.1 | 0 | 141 |  | 1.01 | 1 | -0.0564 | 14.1
CIELOGEN_2G | -0.004 | 1062 | 1 | WEST | YES | 6.1 | 0 | 61 |  | 1 | 1 | -0.0244 | 6.1
CIELOGEN_1G | -0.004 | 1061 | 1 | WEST | YES | 9.9 | 0 | 99 |  | 1 | 1 | -0.0396 | 9.9
L_BUCHAN1_1Y | -0.004 | 7022 | 1 | SOUTH | YES | 14 | 0 | 18 |  | 1 | 1 | -0.056 | 14
LONGSHORT_5 | -0.004 | 1058 | 1 | NORTH | YES | 15 | 0 | 149 |  | 0.95 | 1 | -0.06 | 15
NAV5CT | -0.004 | 11013 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.32 | 80
ROSCOEW_5 | -0.004 | 1049 | 1 | WEST | YES | 20.9 | 0 | 209 |  | 0.99 | 1 | -0.0836 | 20.9
CALENG3G_3G | -0.004 | 1047 | 3 | WEST | YES | 69 | 27 | 69 | 0 | 1.017 | 1 | -0.276 | 69
L_DELAWA1_1Y | -0.004 | 7038 | 2 | WEST | YES | 4.5 | 0 | 30 | 0 | 1 | 1 | -0.018 | 4.5
SNYDERW1A | -0.004 | 6637 | 1 | WEST | YES | 6.3 | 0 | 63 | 0 | 1.025 | 1 | -0.0252 | 6.3
CALENG2G_2G | -0.004 | 1046 | 2 | WEST | YES | 74 | 27 | 74 | 0 | 1.017 | 1 | -0.296 | 74
KINDERMG_2G | -0.004 | 1070 | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0 | 1.01 | 0 | 0 | 0
CALENG1G_1G | -0.004 | 1045 | 1 | WEST | YES | 73 | 27 | 73 | 0 | 1.017 | 1 | -0.292 | 73
MRGNFG_6G | -0.004 | 1044 | F | WEST | YES | 66 | 66 | 66 |  | 0.99 | 1 | -0.264 | 66
TNTNPONE_28 | -0.004 | 39970 | 1 | NORTH | YES | 154 | 30 | 154 |  | 1.04 | 0 | 0 | 0
TNTNPONE_18 | -0.004 | 39960 | 1 | NORTH | YES | 152 | 30 | 152 |  | 1.04 | 0 | 0 | 0
L_BUCHAN1_2Y | -0.004 | 7023 | 2 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
L_BUCHAN1_3Y | -0.004 | 7024 | 3 | SOUTH | YES | 11 | 0 | 15 |  | 1 | 1 | -0.044 | 11
ROSCOEWI_5 | -0.004 | 1057 | 1 | WEST | YES | 12.6 | 0 | 126.5 |  | 0.99 | 1 | -0.0504 | 12.6
L_MARBFA1_2Y | -0.004 | 7029 | 2 | SOUTH | YES | 13 | 0 | 18 |  | 1 | 1 | -0.052 | 13
CIRELLO | -0.004 | 60060 | 1 | WEST | YES | 35 | 0 | 233 | 0 | 1 | 1 | -0.14 | 35
L_MARBFA1_1Y | -0.004 | 7028 | 1 | SOUTH | YES | 0 | 0 | 18 |  | 1 | 1 | 0 | 0
HORSH1 | -0.004 | 60066 | 1 | WEST | YES | 33.3 | 0 | 222 | 0 | 1.005 | 1 | -0.1332 | 33.3
MRGNDG_4G | -0.004 | 1042 | D | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.28 | 70
LOUIS1A | -0.004 | 60063 | 1 | WEST | YES | 25.5 | 0 | 170.2 | 0 | 1.02 | 1 | -0.102 | 25.5
RDCNYNG1 | -0.004 | 36998 | 1 | WEST | YES | 8.4 | 0 | 84 | 0 | 1.01 | 1 | -0.0336 | 8.4
MRGNCG_3G | -0.004 | 1041 | C | WEST | YES | 70 | 69 | 70 |  | 0.99 | 1 | -0.28 | 70
ATKINS7 | -0.004 | 32888 | 1 | NORTH | YES | 0 | 4 | 17 |  | 1.028 | 1 | 0 | 0
ATKINS6 | -0.004 | 32887 | MB | NORTH | YES | 0 | 12 | 51 |  | 1.028 | 1 | 0 | 0
ATKINS3 | -0.004 | 32886 | MB | NORTH | YES | 0 | 5 | 12 |  | 1 | 1 | 0 | 0
TAMUGEN1 | -0.004 | 32798 | 1 | NORTH | YES | 32 | 0 | 32 |  | 1.02 | 1 | -0.128 | 32
PBCTBGE_2G | -0.004 | 1003 | B | WEST | YES | 65 | 65 | 66 | 0 | 1.022 | 1 | -0.26 | 65
MRGNBG_2G | -0.004 | 1040 | B | WEST | YES | 71 | 70 | 71 |  | 0.99 | 1 | -0.284 | 71
L_GASCCR1_1N | -0.004 | 76031 | 1 | WEST | YES | 15 | 0 | 150 | 0 | 1 | 1 | -0.06 | 15
MRGNAG_1G | -0.004 | 1039 | A | WEST | YES | 69 | 69 | 69 |  | 0.99 | 1 | -0.276 | 69
MORGAN5G_5G | -0.004 | 1037 | 5 | WEST | YES | 137 | 40 | 137 |  | 0.99 | 1 | -0.548 | 137
NWPWRG1_1G | -0.004 | 1350 | 1 | WEST | YES | 3.4 | 0 | 34.3 |  | 1.02 | 1 | -0.0136 | 3.4
L_SWEETW1_1N | -0.004 | 71054 | 1 | WEST | YES | 16.1 | 0 | 107.5 | 0 | 1 | 1 | -0.0644 | 16.1
PB6GEN_7G | -0.004 | 1008 | 6 | WEST | YES | 515 | 130 | 515 | 0 | 1.022 | 1 | -2.06 | 515
TIEHVCG_4G | -0.004 | 11024 | 1 | WEST | YES | 149 | 103 | 149 | 0 | 1.017 | 1 | -0.596 | 149
TIEHVCG_3G | -0.004 | 11023 | 1 | WEST | YES | 132 | 103 | 132 | 0 | 1.017 | 1 | -0.528 | 132
AEPWIND_8 | -0.004 | 1354 | 1 | WEST | YES | 15.2 | 0 | 101.2 |  | 1.01 | 1 | -0.0608 | 15.2
TIEHVCG_1G | -0.004 | 11021 | 1 | WEST | YES | 145 | 103 | 145 | 0 | 1.017 | 1 | -0.58 | 145
TIEHVSG_1G | -0.004 | 11020 | 1 | WEST | YES | 211 | 63 | 211 | 0 | 1.017 | 1 | -0.844 | 211
NAV6ST | -0.004 | 11014 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.46 | 115
PB5GEN_6G | -0.004 | 1007 | 5 | WEST | YES | 115 | 40 | 115 | 0 | 1.022 | 1 | -0.46 | 115
NAV3ST | -0.004 | 11011 | 1 | WEST | YES | 115 | 40 | 115 | 0 | 1.017 | 1 | -0.46 | 115
NAV2CT | -0.004 | 11009 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.32 | 80
L_SWEETW1_3N | -0.004 | 71059 | 1 | WEST | YES | 17.8 | 0 | 119 | 0 | 1 | 1 | -0.0712 | 17.8
NAV1CT | -0.004 | 11001 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.32 | 80
PBCTEGE_5G | -0.004 | 1006 | E | WEST | YES | 65 | 65 | 68 | 0 | 1.022 | 1 | -0.26 | 65
L_SWEETW1_4N | -0.004 | 71060 | 1 | WEST | YES | 15.7 | 0 | 105 | 0 | 1 | 1 | -0.0628 | 15.7
PBCTDGE_4G | -0.004 | 1005 | D | WEST | YES | 65 | 65 | 65 | 0 | 1.022 | 1 | -0.26 | 65
TRENTIPP_8 | -0.004 | 1343 | 1 | WEST | YES | 22.5 | 0 | 150 |  | 1.014 | 1 | -0.09 | 22.5
PBCTCGE_3G | -0.004 | 1004 | C | WEST | YES | 62 | 62 | 66 | 0 | 1.022 | 1 | -0.248 | 62
ATKINS4 | -0.004 | 32890 | MB | NORTH | YES | 0 | 5 | 22 |  | 1.031 | 1 | 0 | 0
L_DIVIDE1_1N | -0.004 | 76091 | 1 | WEST | YES | 26.5 | 0 | 375 | 0 | 1 | 1 | -0.106 | 26.5
STANTONW_8 | -0.004 | 1326 | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0 | 1.01 | 1 | -0.0404 | 10.1
L_SWEETW1_2N | -0.004 | 71057 | 1 | WEST | YES | 20.3 | 0 | 135 | 0 | 1 | 1 | -0.0812 | 20.3
NAV4CT | -0.004 | 11012 | 1 | WEST | YES | 80 | 18 | 80 | 0 | 1.017 | 1 | -0.32 | 80
L_BITTCR1_1N | -0.004 | 71051 | 1 | WEST | YES | 5.6 | 0 | 37.5 |  | 1.01 | 1 | -0.0224 | 5.6
HORSH2 | -0.004 | 60068 | 1 | WEST | YES | 27.6 | 0 | 184 | 0 | 1.025 | 1 | -0.1104 | 27.6
AIRTRICITY_8 | -0.004 | 1170 | 1 | WEST | YES | 18 | 0 | 180 | 0 | 1.01 | 1 | -0.072 | 18
PBCTAGE_1G | -0.004 | 1002 | A | WEST | YES | 64 | 64 | 65 | 0 | 1.022 | 1 | -0.256 | 64
CALHN_G1 | -0.004 | 60057 | 1 | WEST | YES | 17.1 | 0 | 114 | 0 | 1.042 | 1 | -0.0684 | 17.1
MCDDONAL_8 | -0.004 | 1333 | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0 | 1.01 | 1 | -0.0856 | 21.4
L_DELAWA1_1Y | -0.004 | 7038 | 1 | WEST | YES | 5.2 | 0 | 35 | 0 | 1 | 1 | -0.0208 | 5.2
ATKINS5 | -0.004 | 32891 | MB | NORTH | YES | 0 | 5 | 25 |  | 1.031 | 1 | 0 | 0
BSP_1 | -0.004 | 1320 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 |  | 1 | 0 | 0 | 0
BUFGGEN | -0.004 | 60058 | 1 | WEST | YES | 18 | 0 | 120 |  | 1 | 1 | -0.072 | 18
VISTRONG1 | -0.003 | 80224 | 1 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 0 | 0 | 0
FTR_GT3_5085 | -0.003 | 48673 | 3 | NORTH | YES | 158 | 0 | 158 | 0 | 1.0319 | 1 | -0.474 | 158
FTR_GT1_5105 | -0.003 | 48671 | 1 | NORTH | YES | 156 | 0 | 156 | 0 | 1.0319 | 1 | -0.468 | 156
SWMESA | -0.003 | 6016 | 1 | WEST | YES | 11.2 | 0 | 75 |  | 1.03 | 1 | -0.0336 | 11.2
FTR_CN4_5095 | -0.003 | 48674 | 4 | NORTH | YES | 380 | 0 | 380 | 0 | 1.0319 | 1 | -1.14 | 380
FOR_4 | -0.003 | 8154 | 4 | SOUTH | YES | 74.6 | 60 | 81 | 0 | 1.03 | 1 | -0.2238 | 74.6
FTR_GT2_5110 | -0.003 | 48672 | 2 | NORTH | YES | 159 | 0 | 159 | 0 | 1.0319 | 1 | -0.477 | 159
KM NEP | -0.003 | 60003 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.036 | 12
FOR_3 | -0.003 | 8153 | 3 | SOUTH | YES | 65.8 | 45 | 73 | 0 | 1.03 | 1 | -0.1974 | 65.8
TNWDWRDU2_8 | -0.003 | 38332 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.0232 | 1 | -0.036 | 12
FOR_9 | -0.003 | 80052 | 9 | SOUTH | YES | 32 | 5 | 32 | 0 | 1.03 | 1 | -0.096 | 32
FOR_10 | -0.003 | 80053 | 10 | SOUTH | YES | 73 | 45 | 73 | 0 | 1.03 | 1 | -0.219 | 73
RIO_DRCS | -0.003 | 60201 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
FOR_5 | -0.003 | 8155 | 5 | SOUTH | YES | 67.5 | 60 | 74 | 0 | 1.03 | 1 | -0.2025 | 67.5
ALCOA_G | -0.003 | 80226 | 1 | SOUTH | YES | 48 | 5 | 48 | 0 | 1.014 | 0 | 0 | 0
KM NWP | -0.003 | 60019 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.036 | 12
KM SWP | -0.003 | 60007 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.03 | 1 | -0.036 | 12
FOR_8 | -0.003 | 80051 | 8 | SOUTH | YES | 28 | 28 | 28 | 0 | 1.015 | 1 | -0.084 | 28
FOR_7 | -0.003 | 8157 | 7 | SOUTH | YES | 46 | 5 | 46 | 0 | 1.03 | 1 | -0.138 | 46
FOR_1 | -0.003 | 8134 | 1 | SOUTH | YES | 56.4 | 45 | 79 | 0 | 1.03 | 1 | -0.1692 | 56.4
FOR_2 | -0.003 | 8138 | 2 | SOUTH | YES | 65.8 | 45 | 80 | 0 | 1.03 | 1 | -0.1974 | 65.8
WDWDU1 | -0.003 | 60016 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.033 | 1 | -0.036 | 12
KM SEP | -0.003 | 60005 | 1 | WEST | YES | 6 | 0 | 40 |  | 1.035 | 1 | -0.018 | 6
GIBN_CREK_G1 | -0.003 | 990 | 1 | NORTH | YES | 464 | 200 | 464 | 0 | 1.0275 | 0 | 0 | 0
FOR_6 | -0.003 | 8156 | 6 | SOUTH | YES | 26 | 5 | 26 | 0 | 1.03 | 1 | -0.078 | 26
VISTRONG2 | -0.003 | 80225 | 2 | SOUTH | YES | 23 | 0 | 23 | 0 | 1.01 | 0 | 0 | 0
UCAR_1 | -0.002 | 8148 | 2 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.01 | 1 | -0.014 | 7
UCAR_2 | -0.002 | 8147 | 10 | SOUTH | YES | 21 | 0 | 28 | 0 | 1.0127 | 1 | -0.042 | 21
CSDR56 | -0.002 | 80139 | 5 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | -0.03 | 15
CSDR7 | -0.002 | 80138 | 7 | SOUTH | YES | 7 | 0 | 7 | 0 | 1.014 | 1 | -0.014 | 7
CSDR11 | -0.002 | 80140 | 11 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.0299 | 1 | -0.078 | 39
CBE_ST34 | -0.002 | 48736 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | -0.207 | 103.5
CBE_GT4 | -0.002 | 48735 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | -0.172 | 86
L_INKSDA1_1Y | -0.002 | 7026 | 1 | SOUTH | YES | 10 | 0 | 14 |  | 1 | 1 | -0.02 | 10
CBE_GT2 | -0.002 | 48732 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | -0.172 | 86
CBE_GT1 | -0.002 | 48731 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | -0.172 | 86
CBE_ST12 | -0.002 | 48733 | 1 | HOUSTON | YES | 103.5 | 0 | 103.5 | 0 | 1.029 | 1 | -0.207 | 103.5
CBE_GT3 | -0.002 | 48734 | 1 | HOUSTON | YES | 86 | 0 | 86 | 0 | 1.029 | 1 | -0.172 | 86
CSDR56 | -0.002 | 80139 | 6 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | -0.078 | 39
CSDR89 | -0.002 | 80137 | 9 | SOUTH | YES | 15 | 0 | 15 | 0 | 1.01 | 1 | -0.03 | 15
CSDR89 | -0.002 | 80137 | 8 | SOUTH | YES | 39 | 0 | 39 | 0 | 1.01 | 1 | -0.078 | 39
DSKY1 | -0.002 | 60018 | 1 | WEST | YES | 12.6 | 0 | 84 | 0 | 1.032 | 1 | -0.0252 | 12.6
ORNNWP1 | -0.002 | 60017 | 1 | WEST | YES | 12 | 0 | 80 |  | 1.027 | 1 | -0.024 | 12
DSKY2 | -0.002 | 60000 | 1 | WEST | YES | 11.5 | 0 | 76.5 |  | 1.039 | 1 | -0.023 | 11.5
THW_5556 | -0.001 | 48887 | F | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
THW_5354 | -0.001 | 48886 | D | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | -0.0166 | 16.6
THW_5354 | -0.001 | 48886 | C | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
THW_5152 | -0.001 | 48885 | B | HOUSTON | YES | 0 | 5 | 55 |  | 1.0319 | 1 | 0 | 0
THW_GT1_GT_1 | -0.001 | 48883 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.043 | 1 | 0 | 0
THW_4344 | -0.001 | 48881 | H | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_4344 | -0.001 | 48881 | G | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_4142 | -0.001 | 48879 | E | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_3334 | -0.001 | 48877 | D | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_3334 | -0.001 | 48877 | C | HOUSTON | YES | 58 | 5 | 58 | 0 | 1.0435 | 1 | -0.058 | 58
THW_3132 | -0.001 | 48875 | B | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
THW_3132 | -0.001 | 48875 | A | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
THW_ST4_ST_4 | -0.001 | 48874 | 4 | HOUSTON | YES | 108 | 19 | 108 | 0 | 1.0435 | 1 | -0.108 | 108
THW_ST3_ST_3 | -0.001 | 48873 | 3 | HOUSTON | YES | 110 | 19 | 110 | 0 | 1.0435 | 1 | -0.11 | 110
CVC_GT4_8005 | -0.001 | 48815 | 4 | HOUSTON | YES | 165 | 91.8 | 165 | 0 | 1.0362 | 1 | -0.165 | 165
CVC_ST5_5040 | -0.001 | 48814 | 1 | HOUSTON | YES | 133 | 91.8 | 133 |  | 1.029 | 1 | -0.133 | 133
CVC_GT1_5035 | -0.001 | 48813 | 1 | HOUSTON | YES | 155 | 91.8 | 155 |  | 1.029 | 1 | -0.155 | 155
CVC_GT3_5045 | -0.001 | 48811 | 3 | HOUSTON | YES | 158 | 91.8 | 158 |  | 1.029 | 1 | -0.158 | 158
PSA_GN1_8165 | -0.001 | 48796 | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0 | 1.0362 | 1 | -0.104 | 104
L_WIRTZ_1G2Y | -0.001 | 7036 | 2 | SOUTH | YES | 18 | 0 | 30 |  | 1 | 1 | -0.018 | 18
L_WIRTZ_1G1Y | -0.001 | 7035 | 1 | SOUTH | YES | 0 | 0 | 29 |  | 1 | 1 | 0 | 0
PSA_GT3_8150 | -0.001 | 48793 | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0 | 1.0362 | 1 | -0.07 | 70
PSA_GT2_8155 | -0.001 | 48792 | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | -0.066 | 66
GBY_GN5_5 | -0.001 | 48690 | 5 | HOUSTON | YES | 298.5 | 81 | 398 | 0 | 1.0362 | 1 | -0.2985 | 298.5
EP_1_2 | -0.001 | 48651 | 2 | HOUSTON | YES | 21 | 10 | 21 | 0 | 1.0362 | 1 | -0.021 | 21
EP_1_2 | -0.001 | 48651 | 1 | HOUSTON | YES | 5 | 0 | 5 | 0 | 1.0362 | 1 | -0.005 | 5
BTE_ST1_8070 | -0.001 | 48598 | 4 | HOUSTON | YES | 234 | 60 | 234 | 0 | 1.0261 | 1 | -0.234 | 234
BTE_GT4_8055 | -0.001 | 48597 | 3 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | -0.163 | 163
BTE_GT3_8045 | -0.001 | 48596 | 2 | HOUSTON | YES | 158 | 130 | 158 | 0 | 1.0261 | 1 | -0.158 | 158
BTE_GT2_8075 | -0.001 | 48595 | 1 | HOUSTON | YES | 163 | 130 | 163 | 0 | 1.0261 | 1 | -0.163 | 163
CHE_GT2_5030 | -0.001 | 48591 | 2 | HOUSTON | YES | 173 | 50 | 173 |  | 1.029 | 1 | -0.173 | 173
TGF_GT1_8000 | -0.001 | 48911 | 1 | HOUSTON | YES | 69.2 | 0 | 69.2 | 0 | 1.029 | 1 | -0.0692 | 69.2
PSA_GT1_8160 | -0.001 | 48791 | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0 | 1.0362 | 1 | -0.065 | 65
PSA_GT5_8140 | -0.001 | 48795 | 5 | HOUSTON | YES | 64 | 20.3 | 64 | 0 | 1.0362 | 1 | -0.064 | 64
PSA_GT4_8145 | -0.001 | 48794 | 4 | HOUSTON | YES | 66 | 20.3 | 66 | 0 | 1.0362 | 1 | -0.066 | 66
AIRCO_G | -0.001 | 80227 | 1 | SOUTH | YES | 7.6 | 0 | 8 | 0 | 1.014 | 0 | 0 | 0
CVC_GT2_5020 | -0.001 | 48812 | 2 | HOUSTON | YES | 159 | 91.8 | 159 |  | 1.029 | 1 | -0.159 | 159
THW_4142 | -0.001 | 48879 | F | HOUSTON | YES | 57 | 5 | 57 | 0 | 1.0435 | 1 | -0.057 | 57
THW_5556 | -0.001 | 48887 | E | HOUSTON | YES | 16.6 | 5 | 58 |  | 1.0319 | 1 | -0.0166 | 16.6
THW_5152 | -0.001 | 48885 | A | HOUSTON | YES | 16.4 | 5 | 57 |  | 1.0319 | 1 | -0.0164 | 16.4
PSA_GT6_8135 | -0.001 | 48797 | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0 | 1.0362 | 1 | -0.059 | 59
SRB_GT211035 | 0 | 48855 | B2 | HOUSTON | YES | 0 | 0 | 12 |  | 1.014 | 1 | 0 | 0
EXN_14GT | 0 | 49838 | 14 | HOUSTON | YES | 140 | 0 | 148 |  | 1.0326 | 1 | 0 | 140
EXN_GT | 0 | 49837 | 4 | HOUSTON | YES | 81 | 21.3 | 86 | 0 | 1.0326 | 1 | 0 | 81
EXN944GT | 0 | 49831 | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0 | 1.0326 | 1 | 0 | 33
EXN943GT | 0 | 49830 | 12 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0 | 19
EXN942GT | 0 | 49829 | 11 | HOUSTON | YES | 20 | 5.4 | 21 | 0 | 1.0326 | 1 | 0 | 20
EXN938GT | 0 | 49826 | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0 | 1.0326 | 1 | 0 | 43
EXN_17GT | 0 | 49805 | 3 | HOUSTON | YES | 31 | 8.3 | 33 |  | 1.0326 | 1 | 0 | 31
EXN_16GT | 0 | 49804 | 2 | HOUSTON | YES | 32 | 8.3 | 34 |  | 1.0326 | 1 | 0 | 32
WAPGT21_GT1 | 0 | 48929 | B1 | HOUSTON | YES | 0 | 0 | 13 |  | 1.05 | 1 | 0 | 0
WAP_GN5_5 | 0 | 48925 | 5 | HOUSTON | YES | 216.6 | 278 | 657 | 0 | 1 | 0 | 0 | 0
WAP_GN4_4 | 0 | 48924 | 4 | HOUSTON | YES | 544 | 217 | 544 |  | 1.0362 | 1 | 0 | 544
WAP_GN3_3 | 0 | 48923 | 3 | HOUSTON | YES | 226 | 93 | 226 |  | 1.0362 | 1 | 0 | 226
WAP_GN2_2 | 0 | 48922 | 2 | HOUSTON | YES | 122.2 | 37 | 163 | 0 | 1.0362 | 1 | 0 | 122.2
WAP_GN1_1 | 0 | 48921 | 1 | HOUSTON | YES | 124.5 | 37 | 166 | 0 | 1.0362 | 1 | 0 | 124.5
SRB_GN2_2 | 0 | 48852 | 2 | HOUSTON | YES | 174 | 26 | 174 | 0 | 1.0217 | 1 | 0 | 174
SRB_GT211035 | 0 | 48855 | B1 | HOUSTON | YES | 0 | 0 | 17 |  | 1.014 | 1 | 0 | 0
SRB_GN4_4 | 0 | 48854 | 4 | HOUSTON | YES | 226 | 35 | 226 |  | 1.0326 | 1 | 0 | 226
SRB_GN3_3 | 0 | 48853 | 3 | HOUSTON | YES | 220 | 35 | 220 |  | 1.0326 | 1 | 0 | 220
SRB_GN1_1 | 0 | 48851 | 1 | HOUSTON | YES | 176 | 26 | 176 | 0 | 1.0217 | 1 | 0 | 176
SOL_GT1 | 0 | 48845 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 |  | 1.0326 | 1 | 0 | 16.2
SJS_GT2_GT2 | 0 | 48842 | 2 | HOUSTON | YES | 49 | 49 | 81 | 0 | 1.0362 | 1 | 0 | 49
L_MCQUEE9_1Y | 0 | 7605 | 3 | SOUTH | YES | 0 | 0 | 2.8 |  | 1.025 | 1 | 0 | 0
L_MCQUEE9_1Y | 0 | 7605 | 2 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
SHELLG3_3020 | 0 | 48822 | 1 | HOUSTON | YES | 39 | 0 | 39 |  | 1.029 | 1 | 0 | 39
SHELLG2 | 0 | 48821 | 2 | HOUSTON | YES | 72 | 34.5 | 72 |  | 1.029 | 1 | 0 | 72
L_MCQUEE9_1Y | 0 | 7605 | 1 | SOUTH | YES | 0 | 0 | 2.4 |  | 1.025 | 1 | 0 | 0
SHELLG1_3015 | 0 | 48820 | 1 | HOUSTON | YES | 71 | 34.5 | 71 |  | 1.029 | 1 | 0 | 71
PHR_GN2_2 | 0 | 48772 | MB | HOUSTON | YES | 0 | 72 | 459 |  | 1.0362 | 0 | 0 | 0
PR_GT1__9040 | 0 | 48761 | 1 | HOUSTON | YES | 35 | 0 | 35 | 0 | 1 | 1 | 0 | 35
PSG_GT3_8060 | 0 | 48742 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0 | 164
PSG_GT2_8040 | 0 | 48741 | 1 | HOUSTON | YES | 164 | 50 | 164 | 0 | 1.0326 | 1 | 0 | 164
PSG_GN2_8050 | 0 | 48740 | 1 | HOUSTON | YES | 178 | 60 | 178 | 0 | 1.0326 | 1 | 0 | 178
MNS_GT | 0 | 48730 | 1 | HOUSTON | YES | 46.1 | 0 | 46.1 | 0 | 1.029 | 1 | 0 | 46.1
GBY_83841065 | 0 | 48693 | F | HOUSTON | YES | 20 | 20 | 52 | 0 | 1.0362 | 1 | 0 | 20
GBY_83841065 | 0 | 48693 | E | HOUSTON | YES | 20 | 20 | 56 | 0 | 1.0362 | 1 | 0 | 20
GBY_81821075 | 0 | 48692 | D | HOUSTON | YES | 20 | 20 | 54 | 0 | 1.0362 | 1 | 0 | 20
GBY_81821075 | 0 | 48692 | C | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0 | 48
GBY_73741085 | 0 | 48691 | B | HOUSTON | YES | 47 | 20 | 47 | 0 | 1.0362 | 1 | 0 | 47
GBY_73741085 | 0 | 48691 | A | HOUSTON | YES | 48 | 20 | 48 | 0 | 1.0362 | 1 | 0 | 48
DPEC_GT45070 | 0 | 48644 | 4 | HOUSTON | YES | 158 | 98 | 158 | 0 | 1.0319 | 1 | 0 | 158
DPEC_GT35010 | 0 | 48643 | 3 | HOUSTON | YES | 160 | 98 | 160 | 0 | 1.0319 | 1 | 0 | 160
DPEC_GT25025 | 0 | 48642 | 2 | HOUSTON | YES | 156 | 98 | 156 | 0 | 1.0319 | 1 | 0 | 156
DIB_GT3_8090 | 0 | 48614 | 4 | HOUSTON | YES | 77.2 | 15 | 77.2 | 0 | 1.0326 | 1 | 0 | 77.2
DIB_ST1_8085 | 0 | 48613 | 3 | HOUSTON | YES | 69 | 0 | 69 | 0 | 1.0326 | 1 | 0 | 69
DIB_GT2_8075 | 0 | 48612 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0 | 65
DIB_GT1_8080 | 0 | 48611 | 1 | HOUSTON | YES | 64 | 0 | 64 | 0 | 1.0326 | 1 | 0 | 64
CHE_GN4_8025 | 0 | 48594 | 4 | HOUSTON | YES | 142 | 60 | 142 | 0 | 1.0362 | 1 | 0 | 142
CHE_GT1_8015 | 0 | 48593 | 1 | HOUSTON | YES | 173 | 50 | 173 | 0 | 1.0362 | 1 | 0 | 173
CBY_GN2_2 | 0 | 48582 | 2 | HOUSTON | YES | 751 | 110 | 751 | 0 | 1.0435 | 1 | 0 | 751
CBY_GN1_1 | 0 | 48581 | 1 | HOUSTON | YES | 748 | 108 | 748 | 0 | 1.0435 | 1 | 0 | 748
CTL_GN2_8155 | 0 | 48565 | 5 | HOUSTON | YES | 11 | 3.4 | 11 |  | 1.0362 | 1 | 0 | 11
CTL_GN1_8145 | 0 | 48564 | 4 | HOUSTON | YES | 55 | 12.9 | 55 |  | 1.0362 | 1 | 0 | 55
L_FERGUS1_1Y | 0 | 7000 | 1 | SOUTH | YES | 399 | 65 | 421 | 0 | 1.015 | 1 | 0 | 399
CTL_GT4_8140 | 0 | 48563 | 3 | HOUSTON | YES | 94 | 30.3 | 94 |  | 1.0362 | 1 | 0 | 94
CTL_GT3_8135 | 0 | 48562 | 2 | HOUSTON | YES | 91 | 30.3 | 91 |  | 1.0362 | 1 | 0 | 91
CTL_GT2_8130 | 0 | 48561 | 1 | HOUSTON | YES | 103 | 30.3 | 103 |  | 1.0362 | 1 | 0 | 103
CAL_ST1_8000 | 0 | 48552 | 2 | HOUSTON | YES | 65 | 0 | 65 | 0 | 1.0326 | 1 | 0 | 65
CAL_GT1_8045 | 0 | 48551 | 1 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0326 | 1 | 0 | 152
DPEC_GT15040 | 0 | 48641 | 1 | HOUSTON | YES | 162 | 98 | 162 | 0 | 1.0319 | 1 | 0 | 162
BYU_GT4_8065 | 0 | 48534 | 4 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0 | 65
BYU_GT3_8060 | 0 | 48533 | 3 | HOUSTON | YES | 67 | 0 | 67 |  | 1.0362 | 1 | 0 | 67
BYU_GT2_8055 | 0 | 48532 | 2 | HOUSTON | YES | 62 | 0 | 62 |  | 1.0362 | 1 | 0 | 62
DPEC_ST55065 | 0 | 48645 | 5 | HOUSTON | YES | 282 | 0 | 282 | 0 | 1.0319 | 1 | 0 | 282
BYU_GT1_8075 | 0 | 48531 | 1 | HOUSTON | YES | 65 | 0 | 65 |  | 1.0362 | 1 | 0 | 65
LPE_GT4_8085 | 0 | 48514 | 4 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0 | 41
LPE_GT3_8080 | 0 | 48513 | 3 | HOUSTON | YES | 41 | 0 | 41 | 0 | 1.0362 | 1 | 0 | 41
SJS_GT1_GT1 | 0 | 48841 | 1 | HOUSTON | YES | 49 | 49 | 83 | 0 | 1.0362 | 1 | 0 | 49
LPE_GT2_8075 | 0 | 48512 | 2 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0 | 42
LPE_GT1_8070 | 0 | 48511 | 1 | HOUSTON | YES | 42 | 0 | 42 | 0 | 1.0362 | 1 | 0 | 42
AK_GT1__8040 | 0 | 48510 | 1 | HOUSTON | YES | 34 | 8.1 | 34 |  | 1.029 | 1 | 0 | 34
APD_GT1_8005 | 0 | 48500 | 1 | HOUSTON | YES | 140 | 54.6 | 140 |  | 1.0362 | 1 | 0 | 140
TNSCLP3___8 | 0 | 39790 | 1 | HOUSTON | YES | 111 | 20 | 111 | 0 | 1.027 | 1 | 0 | 111
TNSCLP4___8 | 0 | 39775 | 1 | HOUSTON | YES | 115 | 20 | 115 | 0 | 1.04 | 1 | 0 | 115
SHELLG3_3020 | 0 | 48822 | 2 | HOUSTON | YES | 30 | 0 | 30 |  | 1.029 | 1 | 0 | 30
TNSCLP2___8 | 0 | 39770 | 1 | HOUSTON | YES | 117 | 20 | 117 | 0 | 1.04 | 1 | 0 | 117
TNSCLP1___8 | 0 | 39760 | 1 | HOUSTON | YES | 116 | 20 | 116 | 0 | 1.04 | 1 | 0 | 116
TNDOWCGNGG8 | 0 | 39480 | 1 | HOUSTON | YES | 30 | 10 | 30 | 0 | 1.0437 | 1 | 0 | 30
TNDOWCGNSG8 | 0 | 39470 | 1 | HOUSTON | YES | 32 | 10 | 32 | 0 | 1.0437 | 1 | 0 | 32
TNSLCGN1__8 | 0 | 39190 | 1 | HOUSTON | YES | 30 | 10 | 30 |  | 1.025 | 1 | 0 | 30
TNTXCTY4CG8 | 0 | 38714 | 1 | HOUSTON | YES | 103 | 59 | 103 | 0 | 1.044 | 1 | 0 | 103
TNTXCTY3CG8 | 0 | 38713 | 1 | HOUSTON | YES | 85 | 59 | 85 | 0 | 1.044 | 1 | 0 | 85
TNTXCTY2CG8 | 0 | 38712 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0 | 1.044 | 1 | 0 | 102
TNTXCTY1CG8 | 0 | 38711 | 1 | HOUSTON | YES | 105 | 59 | 105 | 0 | 1.044 | 1 | 0 | 105
TNBP_CGN4_8 | 0 | 38690 | 3 | HOUSTON | YES | 40 | 0 | 40 | 0 | 1.0435 | 1 | 0 | 40
TNBPAMCG4_8 | 0 | 38614 | 4 | HOUSTON | YES | 96 | 0 | 96 | 0 | 1.0435 | 1 | 0 | 96
TNBPAMCG3_8 | 0 | 38613 | 3 | HOUSTON | YES | 152 | 0 | 152 | 0 | 1.0435 | 1 | 0 | 152
TNBPAMCG2_8 | 0 | 38612 | 2 | HOUSTON | YES | 150 | 0 | 150 | 0 | 1.0435 | 1 | 0 | 150
TNBPAMCG1_8 | 0 | 38611 | 1 | HOUSTON | YES | 155 | 0 | 155 | 0 | 1.0435 | 1 | 0 | 155
TNBP_CGN3_8 | 0 | 38600 | 5 | HOUSTON | YES | 53 | 0 | 53 | 0 | 1.0435 | 1 | 0 | 53
TNBP_CGN2_8 | 0 | 38590 | 2 | HOUSTON | YES | 66 | 0 | 66 | 0 | 1.0435 | 1 | 0 | 66
RAYBURNCC8 | 0 | 5512 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0 | 50
TNBP_CGN1_8 | 0 | 38580 | 1 | HOUSTON | YES | 60 | 0 | 60 | 0 | 1.0435 | 1 | 0 | 60
RAYBURNCC7 | 0 | 5511 | 1 | SOUTH | YES | 49 | 18.2 | 49 | 0 | 1.02 | 1 | 0 | 49
RAYBURNCC10 | 0 | 5509 | 1 | SOUTH | YES | 40 | 5.2 | 40 | 0 | 1.02 | 1 | 0 | 40
RAYBURNCC9 | 0 | 5508 | 1 | SOUTH | YES | 50 | 18.2 | 50 | 0 | 1.02 | 1 | 0 | 50
EXN_15GT | 0 | 49803 | 1 | HOUSTON | YES | 33 | 8.3 | 35 |  | 1.0326 | 1 | 0 | 33
EXN941GT | 0 | 49828 | 10 | HOUSTON | YES | 19 | 5.4 | 20 | 0 | 1.0326 | 1 | 0 | 19
FRNDDRCS | 0 | 60202 | SC | WEST | YES | 0 | 0 | 0 | 0 | 1.0259 | 1 | 0 | 0
EXN945GT | 0 | 49832 | 9 | HOUSTON | YES | 19 | 9.2 | 20 | 0 | 1.0326 | 1 | 0 | 19
WAP_GN8_8 | 0.001 | 48928 | 8 | HOUSTON | YES | 603 | 275 | 603 |  | 1.035 | 0 | 0 | 0
WAP_GN7_7 | 0.001 | 48927 | 7 | HOUSTON | YES | 567 | 277 | 567 |  | 1.035 | 0 | 0 | 0
WAP_GN6_6 | 0.001 | 48926 | 6 | HOUSTON | YES | 645 | 280 | 645 |  | 1.035 | 0 | 0 | 0
BVE_ST1_GN1 | 0.001 | 48523 | 3 | HOUSTON | YES | 246 | 0 | 246 |  | 1.035 | 1 | 0.246 | 246
BVE_GT2_5035 | 0.001 | 48522 | 2 | HOUSTON | YES | 170 | 0 | 170 |  | 1.035 | 1 | 0.17 | 170
BVE_GT1_GT1 | 0.001 | 48521 | 1 | HOUSTON | YES | 172 | 0 | 172 |  | 1.035 | 1 | 0.172 | 172
BSF_GT1_8070 | 0.002 | 48520 | 2 | HOUSTON | YES | 10 | 0 | 10 | 0 | 1.0326 | 1 | 0.02 | 10
BSF_GT1_8070 | 0.002 | 48520 | 1 | HOUSTON | YES | 72 | 0 | 72 | 0 | 1.0326 | 1 | 0.144 | 72
RAYBURNGEN2 | 0.002 | 5506 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN1 | 0.002 | 5505 | 1 | SOUTH | YES | 0 | 1 | 11 |  | 1.015 | 1 | 0 | 0
RAYBURNGEN3 | 0.002 | 5503 | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0 | 1.015 | 1 | 0.0124 | 6.2
DOW49000 | 0.003 | 49869 | 45 | HOUSTON | YES | 59 | 0 | 94 |  | 1 | 0 | 0 | 0
DOW42000 | 0.003 | 49866 | 42 | HOUSTON | YES | 11 | 0 | 18 |  | 1 | 0 | 0 | 0
DOW41000 | 0.003 | 49865 | 41 | HOUSTON | YES | 31 | 0 | 50 |  | 1 | 0 | 0 | 0
DOW39100 | 0.003 | 49862 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0 | 1 | 0 | 0 | 0
DOW38300 | 0.003 | 49860 | 32 | HOUSTON | YES | 63 | 0 | 101 |  | 1 | 0 | 0 | 0
DOW38200 | 0.003 | 49859 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0 | 1 | 0 | 0 | 0
DOW38100 | 0.003 | 49858 | 31 | HOUSTON | YES | 45 | 0 | 71.4 |  | 1 | 0 | 0 | 0
DOW17000 | 0.003 | 49851 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0 | 1 | 0 | 0 | 0
DOW39200 | 0.003 | 49863 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0 | 1 | 0 | 0 | 0
DOW61000 | 0.003 | 49870 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0 | 1 | 0 | 0 | 0
DOW82000 | 0.003 | 49884 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW65000 | 0.003 | 49876 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0 | 1 | 0 | 0 | 0
DOW84000 | 0.003 | 49886 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0 | 0.98 | 0 | 0 | 0
DOW83000 | 0.003 | 49885 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0 | 1 | 0 | 0 | 0
DOW81000 | 0.003 | 49882 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0 | 1 | 0 | 0 | 0
DOW67000 | 0.003 | 49878 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0 | 1 | 0 | 0 | 0
DOW66000 | 0.003 | 49877 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0 | 1 | 0 | 0 | 0
DOW64000 | 0.003 | 49873 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0 | 1 | 0 | 0 | 0
DOW63000 | 0.003 | 49872 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0 | 1 | 0 | 0 | 0
DOW62000 | 0.003 | 49871 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0 | 1 | 0 | 0 | 0
STP_GN2___2 | 0.005 | 5912 | 2 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
STP_GN1___1 | 0.005 | 5911 | 1 | SOUTH | YES | 1282 | 1249 | 1282 | 0 | 1.0406 | 0 | 0 | 0
BEEVILLE | 0.007 | 88198 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0068 | 1 | 0 | 0
CLO_1 | 0.008 | 8161 | 1 | SOUTH | YES | 633 | 200 | 633 | 0 | 1.03 | 0 | 0 | 0
ICPGN#3 | 0.012 | 8932 | 3 | SOUTH | YES | 127 | 0 | 127 | 0 | 1.03 | 1 | 1.524 | 127
REYSHR_G | 0.012 | 80223 | 1 | SOUTH | YES | 12 | 0 | 12 | 0 | 1.032 | 0 | 0 | 0
ICPGN#2 | 0.012 | 8931 | 2 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.03 | 1 | 1.8 | 150
ICPGN#1 | 0.012 | 8930 | 1 | SOUTH | YES | 149 | 0 | 149 | 0 | 1.03 | 1 | 1.788 | 149
LGEGN#3 | 0.012 | 8928 | 3 | SOUTH | YES | 91 | 0 | 100 | 0 | 1.03 | 1 | 1.092 | 91
LGEGN#2 | 0.012 | 8927 | 2 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.836 | 153
LGEGN#1 | 0.012 | 8926 | 1 | SOUTH | YES | 158 | 0 | 158 | 0 | 1.03 | 1 | 1.896 | 158
CNOPST1 | 0.013 | 8562 | 3 | SOUTH | YES | 153 | 0 | 153 | 0 | 1.03 | 1 | 1.989 | 153
CNOPGT2 | 0.013 | 8561 | 2 | SOUTH | YES | 165 | 0 | 165 | 0 | 1.03 | 1 | 2.145 | 165
CNOPGT1 | 0.013 | 8560 | 1 | SOUTH | YES | 164 | 0 | 164 | 0 | 1.03 | 1 | 2.132 | 164
VAL_2 | 0.013 | 8507 | 2 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.325 | 25
VAL_1 | 0.013 | 8506 | 1 | SOUTH | YES | 25 | 0 | 25 | 0 | 1.005 | 1 | 0.325 | 25
KOCHREF2 | 0.013 | 8461 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.014 | 1 | 0.494 | 38
COSW_2 | 0.013 | 8457 | 2 | SOUTH | YES | 14 | 0 | 14 | 0 | 1.027 | 1 | 0.182 | 14
COSW_1 | 0.013 | 8456 | 1 | SOUTH | YES | 20 | 0 | 20 | 0 | 1.027 | 1 | 0.26 | 20
CEL_B_1 | 0.014 | 8517 | 1 | SOUTH | YES | 29 | 0 | 29 | 0 | 1.02 | 1 | 0.406 | 29
STARCO_1 | 0.014 | 8511 | 1 | SOUTH | YES | 38 | 0 | 38 | 0 | 1.024 | 1 | 0.532 | 38
DAV_2 | 0.014 | 8460 | 2 | SOUTH | YES | 340 | 50 | 340 | 0 | 1.0223 | 1 | 4.76 | 340
DAV_1 | 0.014 | 8459 | 1 | SOUTH | YES | 339 | 50 | 339 | 0 | 1.0223 | 1 | 4.746 | 339
FGNTS201 | 0.015 | 8935 | 3 | SOUTH | YES | 172 | 0 | 172 | 0 | 1.03 | 1 | 2.58 | 172
FALFURRI | 0.015 | 88508 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.01 | 1 | 0 | 0
SI_RAY10 | 0.015 | 5935 | 10 | SOUTH | YES | 47 | 10 | 47 |  | 1.025 | 1 | 0.705 | 47
SI_RAY5 | 0.015 | 5934 | 5 | SOUTH | YES | 10 | 10 | 15 | 0 | 1.025 | 1 | 0.15 | 10
SI_RAY6 | 0.015 | 5933 | 6 | SOUTH | YES | 19 | 10 | 19 | 0 | 1.025 | 1 | 0.285 | 19
SI_RAY9 | 0.015 | 5932 | 9 | SOUTH | YES | 38 | 32 | 38 | 0 | 1.025 | 1 | 0.57 | 38
HECN3 | 0.015 | 8983 | 3 | SOUTH | YES | 169 | 0 | 169 | 0 | 1.0304 | 1 | 2.535 | 169
HECN2 | 0.015 | 8982 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 2.22 | 148
HECN1 | 0.015 | 8981 | 1 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.0304 | 1 | 2.22 | 148
MVGN#3 | 0.015 | 8938 | 3 | SOUTH | YES | 257 | 0 | 257 | 0 | 1.0304 | 1 | 3.855 | 257
MVGN#2 | 0.015 | 8937 | 2 | SOUTH | YES | 205 | 0 | 205 | 0 | 1.0304 | 1 | 3.075 | 205
MVGN#1 | 0.015 | 8936 | 1 | SOUTH | YES | 210 | 0 | 210 | 0 | 1.0304 | 1 | 3.15 | 210
SLURR | 0.015 | 88241 | DC | SOUTH | YES | 0 | -150 | 150 |  | 1.03 | 0 | 0 | 0
FGNTS101 | 0.015 | 8934 | 2 | SOUTH | YES | 146 | 0 | 146 | 0 | 1.03 | 1 | 2.19 | 146
FGNTS001 | 0.015 | 8933 | 1 | SOUTH | YES | 142 | 0 | 142 | 0 | 1.03 | 1 | 2.13 | 142
MILHWYS | 0.015 | 80003 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0168 | 1 | 0 | 0
FALCONHYDRO1 | 0.016 | 8048 | 1 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.048 | 3
FALCONHYDRO3 | 0.016 | 5729 | 3 | SOUTH | YES | 2.8 | 0 | 11 | 0 | 1.02 | 1 | 0.0448 | 2.8
FALCONHYDRO2 | 0.016 | 5728 | 2 | SOUTH | YES | 3 | 0 | 12 | 0 | 1.02 | 1 | 0.048 | 3
AMISTADHDRO2 | 0.017 | 8033 | 2 | SOUTH | YES | 13 | 13 | 25 | 0 | 1.035 | 1 | 0.221 | 13
AMISTADHDRO1 | 0.017 | 8032 | 1 | SOUTH | YES | 16.5 | 13 | 33 | 0 | 1.035 | 1 | 0.2805 | 16.5
ZAPATA | 0.017 | 88299 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.024 | 1 | 0 | 0
HAMILTON | 0.017 | 88253 | 1 | SOUTH | YES | 0 | 0 | 0 | 0 | 1.04 | 1 | 0 | 0
CIDINDUS | 0.019 | 86105 | 1 | SOUTH | YES | 0 | -500 | 500 | 0 | 1.01 | 0 | 0 | 0
LAR | 0.019 | 80012 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.023 | 1 | 0 | 0
EPLVT1 | 0.019 | 80010 | F | SOUTH | YES | 0 | 0 | 0 | 0 | 1.0376 | 1 | 0 | 0
LAR_3 | 0.019 | 8288 | 3 | SOUTH | YES | 78.8 | 25 | 105 |  | 1.023 | 1 | 1.4972 | 78.8
LAR_2 | 0.019 | 8287 | 2 | SOUTH | YES | 9 | 9 | 32 |  | 1.023 | 1 | 0.171 | 9
LAR_1 | 0.019 | 8285 | 1 | SOUTH | YES | 16 | 9 | 32 | 0 | 1.038 | 1 | 0.304 | 16
ELPS | 0.019 | 8262 | 1 | SOUTH | YES | 6 | 6 | 6 | 0 | 1.039 | 1 | 0.114 | 6
PEARSALLGEN3 | 0.026 | 5892 | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0 | 1.01 | 1 | 0.1612 | 6.2
PEARSALLGEN2 | 0.026 | 5891 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.1612 | 6.2
PEARSALLGEN1 | 0.026 | 5890 | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0 | 1.01 | 1 | 0.1612 | 6.2
SANMIGUELGEN | 0.03 | 5903 | 1 | SOUTH | YES | 396 | 180 | 396 | 0 | 1.033 | 0 | 0 | 0
JKS1 | 0.034 | 5401 | 1 | SOUTH | YES | 560 | 100 | 560 | 0 | 1.0222 | 0 | 0 | 0
LCPCT4 | 0.034 | 5269 | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 1.53 | 45
LCPCT3 | 0.034 | 5268 | 3 | SOUTH | YES | 44 | 23.1 | 44 | 0 | 1.0249 | 1 | 1.496 | 44
LCPCT2 | 0.034 | 5267 | 2 | SOUTH | YES | 46 | 23.1 | 46 | 0 | 1.0249 | 1 | 1.564 | 46
LCPCT1 | 0.034 | 5266 | 1 | SOUTH | YES | 45 | 23.1 | 45 | 0 | 1.0249 | 1 | 1.53 | 45
LCP4 | 0.034 | 5265 | 4 | SOUTH | YES | 95 | 25 | 95 | 0 | 1.0249 | 1 | 3.23 | 95
LCP3 | 0.034 | 5264 | 3 | SOUTH | YES | 58 | 20 | 58 | 0 | 1.0249 | 1 | 1.972 | 58
VHB3 | 0.034 | 5028 | 3 | SOUTH | YES | 397 | 60 | 397 | 0 | 1.0233 | 1 | 13.498 | 397
VHB2 | 0.034 | 5027 | 2 | SOUTH | YES | 220 | 40 | 220 | 0 | 1.0233 | 1 | 7.48 | 220
VHB1 | 0.034 | 5026 | 1 | SOUTH | YES | 206 | 40 | 206 | 0 | 1.0233 | 1 | 7.004 | 206
AVR1_CT2 | 0.035 | 5478 | 1 | SOUTH | YES | 145 | 90 | 145 | 0 | 1.0232 | 1 | 5.075 | 145
AVR1_ST1 | 0.035 | 5477 | 1 | SOUTH | YES | 164 | 138 | 164 | 0 | 1.0232 | 1 | 5.74 | 164
AVR1_CT1 | 0.035 | 5476 | 1 | SOUTH | YES | 150 | 90 | 150 | 0 | 1.0232 | 1 | 5.25 | 150
OWS2 | 0.035 | 5397 | 2 | SOUTH | YES | 379 | 80 | 379 | 0 | 1.027 | 1 | 13.265 | 379
OWS1 | 0.035 | 5396 | 1 | SOUTH | YES | 417 | 80 | 417 | 0 | 1.027 | 1 | 14.595 | 417
WBT4 | 0.037 | 5439 | 4 | SOUTH | YES | 151 | 40 | 151 | 0 | 1.01 | 1 | 5.587 | 151
WBT3 | 0.037 | 5438 | 3 | SOUTH | YES | 96 | 25 | 96 | 0 | 1.01 | 1 | 3.552 | 96
WBT2 | 0.037 | 5437 | 2 | SOUTH | YES | 80 | 25 | 80 | 0 | 1.01 | 1 | 2.96 | 80
WBT1 | 0.037 | 5436 | 1 | SOUTH | YES | 25.5 | 20 | 51 | 0 | 1.01 | 1 | 0.9435 | 25.5
JTD2 | 0.037 | 5112 | 2 | SOUTH | YES | 406 | 80 | 406 | 0 | 1.0215 | 0 | 0 | 0
JTD1 | 0.037 | 5111 | 1 | SOUTH | YES | 403 | 80 | 403 | 0 | 1.0215 | 0 | 0 | 0
L_GUADGE1_6Y | 0.04 | 7805 | 6 | SOUTH | YES | 204 | 30 | 204 | 0 | 1.02 | 1 | 8.16 | 204
L_GUADGE1_5Y | 0.04 | 7804 | 5 | SOUTH | YES | 183 | 30 | 183 | 0 | 1.02 | 1 | 7.32 | 183
L_GUADGE1_4Y | 0.04 | 7803 | 4 | SOUTH | YES | 149 | 30 | 149 | 0 | 1.02 | 1 | 5.96 | 149
L_GUADGE1_3Y | 0.04 | 7802 | 3 | SOUTH | YES | 146 | 30 | 146 | 0 | 1.02 | 1 | 5.84 | 146
L_GUADGE1_2Y | 0.04 | 7801 | 2 | SOUTH | YES | 139 | 30 | 139 | 0 | 1.02 | 1 | 5.56 | 139
L_GUADGE1_1Y | 0.04 | 7800 | 1 | SOUTH | YES | 151 | 30 | 151 | 0 | 1.02 | 1 | 6.04 | 151
L_RIONOG1S1Y | 0.045 | 7813 | 4 | SOUTH | YES | 293 | 0 | 293 | 0 | 1.02 | 1 | 13.185 | 293
L_RIONOG1G3Y | 0.045 | 7812 | 3 | SOUTH | YES | 150 | 0 | 150 | 0 | 1.02 | 1 | 6.75 | 150
L_RIONOG1G2Y | 0.045 | 7811 | 2 | SOUTH | YES | 148 | 0 | 148 | 0 | 1.02 | 1 | 6.66 | 148
L_RIONOG1G1Y | 0.045 | 7810 | 1 | SOUTH | YES | 147 | 0 | 147 | 0 | 1.02 | 1 | 6.615 | 147
L_SCHUMA8_1Y | 0.049 | 7609 | 1 | SOUTH | YES | 0 | 0 | 4 |  | 1 | 1 | 0 | 0
L_CANYHY8_1Y | 0.049 | 7487 | 1 | SOUTH | YES | 0 | 0 | 6 |  | 1 | 1 | 0 | 0
L_HAYSEN1_4Y | 0.049 | 7017 | 4 | SOUTH | YES | 229 | 74 | 229 | 0 | 1.008 | 1 | 11.221 | 229
L_HAYSEN1_3Y | 0.049 | 7016 | 3 | SOUTH | YES | 226 | 74 | 226 | 0 | 1.008 | 1 | 11.074 | 226
L_HAYSEN1_2Y | 0.049 | 7015 | 2 | SOUTH | YES | 224 | 74 | 224 | 0 | 1.008 | 1 | 10.976 | 224
L_HAYSEN1_1Y | 0.049 | 7014 | 1 | SOUTH | YES | 223 | 74 | 223 | 0 | 1.008 | 1 | 10.927 | 223