Draft OWG Meeting Notes 05/21/08

9:30 Meeting opened with Antitrust Admonition

- ROS Meeting Notes

  - Black Start Plan has been pushed back to OWG.

  - EECP Step 2 results Actions Items given to OWG.

  - Nodal has been delayed – currently stated by 5 weeks.

- Meeting notes approved from April.

- Thuy Huynh gave the highlights of the April Operations Report.

  - Ross asked whether or not new SPSs will be identified in the monthly operations report.  SPSs are provided publicly on the ERCOT website.

- Stan Morris gave the Operations Task Force update.

  - The Hurricane Drill on May 14th went well.  Only issue brought up from the drill was the hotline call situation.  Wrong numbers at first and was not identified as an all call or just QSEs or TDSPs.

  - Winter drill will be in ’09.

    - Glenn Hemperley gave the Black Start Task Force update.

  - ROS bounced back the recommendation that OWG drop the study in taking a look at analyzing the black start plan.

  - Hemperley mentions that ERCOT did mention that ERCOT’s current study does satisfy NERC requirements.

  - Jack however says that the ERCOT study is based on a steady state overview – and needs to be looked at as transient.

  - ERCOT’s black start plan has to be taken look at as whether or not it is feasible to bring things back as indicated in the plan.  Resolve the issue of whether or not the plan satisfies the criteria in the NERC EOP standard.

  - Next meeting is June 10th – Black Start Task Force will discuss the issue more thoroughly.

  - Dumas mentions that ERCOT extensively looks at the different situations and through black start testing every year.

  - ROS gave OWG two months – and will be discussed at the June/July meeting.

  - Black Start Plan Proposals are due June 1st.  Won’t be announced though till around August.

- Mark Henry gave the Texas RE update

  - TRE is going to take over the 2009 ERCOT Operating Seminar.  Mark doesn’t have any comments and currently there is interest in the group to get the seminar group together.  Lindley Ellisor will be contacting OWG to see who to make sure who is going to be involved with the seminar.  Diana Leese will be helping out with the seminar.  This seminar will be a number of topics of interest – “tutorial” – Operator awareness.

  - TRE – has acquired more requirements from NERC – formed from the original ERCOT compliance.  It’s about verifying reliability.  They are more checkpoints Texas RE has been handling – TAS, Readiness audits, etc.

  - First meeting are usually in July – seminar mailing list should still be around.

  - ERCOT certification session and scoring…should TRE should be involved with the testing aspect?  Mark will bring more information on this next month.

  - Action Item: Mark will bring more details on the seminar at the next meeting.

- Colleen Frosch gave the new bulletins from System Operating Report

  - Changed expiration date on OOME of jointly owned units.

- John Jonte gave the Operating Guides Task Force update.

  - NOGRR 20 & 21 – Synchronizing language.  Impact Analysis will be available next month.

  - OGRR 208 - Low Voltage Ride Through:

    - Issues should involve discussion with AEP and Oncor and would like to have them present at the meeting to help resolve the problems.

    - Aware of the two different graphs available.

    - Next OGRTF will take a look at it more extensively next month – OWG will vote next month and the impact analysis the next.  LCRA and Oncor will make sure they will have representatives.  AEP will have a rep – (Dennis Kunkel)

    - Vendor feedback mentions 3 seconds and 1.75 seconds is a significant issue.  Fossil fuel & gas turbines in terms of the 3 seconds – and they would not be able to meet 3 seconds – would require more $$.  The FERC order does not have a curve.

    - WECC is taking a look at high and low voltage ride-through.

    - Mark Henry agrees something should be played in 661.  Technology would get dumped here because the rest of the states don’t allow it.

    - Wind-only will speed it through the process.  Would be feasible to have a follow up OGR for other units.

    - Warren Lasher (Planning) agrees with something done very quickly – all generators would take significantly more amount of time. A deadline would be needed when grandfathering would expire.  Not all the FERC language applies for ERCOT.  Planning would like to see a blanket standard between generator and the TO – rather than different clearing time and different voltages leading to different relaying concerns.  TSP would perform the study but would need to make sure it is communicated with ERCOT.  i.e. CREZ lines, etc. Inconsistent approach based on turbine by turbine basis.

    - Action item: John Jonte will take a look at fault studies.  Second OGR?

- EECP Directive from ROS.

  - Appeal issues: Should the media appeal be flexible?  If it is flexible before the EECP – ERCOT can issue it early.

  - Appeal on February 26th would have resulted in an overshoot.  PRR 301 – starts at step 1.  “May” has been added to the PRR for the steps of EECP.

  - With “may” then ERCOT won’t be really required to take action – but without may it assures something will be done.

  - Certain things MUST happen and others can be to the operator’s discretion.

  - Discuss ramp rates: Dumas presented the instantaneous ramps from wind generation.  Ramp within 10 minutes?  Stair steps due to the inability to ramp slower.  Was decided a maximum 5% per minute of nameplate rating.

  - Going to require an OGR or protocol.  Dumas (ERCOT) will submit an OGR – but will look into whether it needs to be an OGR or PRR.

- John Jonte addressed the Relay Misoperation Market Notice

  - Brazos, LCRA, CPS Garland Power and Light, AEP, Oncor, CNP, TNMPA and Mark (Texas RE) will have a conference call with Leo Villanueva.

Meeting is at the Taylor Room TCC1 253 on June 18th, 2008.  Next few meetings will be at the Taylor (through October).