## Notes
Notes:
The SSWG 2008 summer peak case updated March 8, 2008 was used as the base case for the analysis
The areas in the case were modified to be the 2008 CM zones
PTDF Sheets:
There is a PTDF Sheet for North-South, West-North, and North-Houston CSCs
South-North and North-West PTDFs will be the same as North-South and West-North respectively, but with the opposite sign
PTDFs were calculated for the CSC and all CREs in the base case (n-0) and under the contingency of the CSC and each CRE
PTDFs were calculated by defining a CM zone to CM zone transfer - only "moveable" units were used in the transfer calculation
The 3 plants that had the highest shift factor in each direction across the CREs was calculated for the base case (n-0) and for the contingency of the CSC
Column A is a reference contingency number - see the Contingency sheets for definitions of the contingencies
Column B is the monitored element
Column C is the long name of the contingency
Column D is the Power Transfer Distribution Factor (PTDF) given as a percentage
Column F is the name of the plant that has the highest shift factor in the positive direction on the element for the given contingency
Column G is the shift factor of the plant listed in column F on the element for the given contingency
Column H is the name of the plant that has the second highest shift factor in the positive direction on the element for the given contingency
Column I is the shift factor of the plant listed in column H on the element for the given contingency
Column J is the name of the plant that has the third highest shift factor in the positive direction on the element for the given contingency
Column K is the shift factor of the plant listed in column J on the element for the given contingency
Column L is the name of the plant that has the highest shift factor in the negative direction on the element for the given contingency
Column M is the shift factor of the plant listed in column L on the element for the given contingency
Column N is the name of the plant that has the second highest shift factor in the negative direction on the element for the given contingency
Column O is the shift factor of the plant listed in column N on the element for the given contingency
Column P is the name of the plant that has the third highest shift factor in the negative direction on the element for the given contingency
Column Q is the shift factor of the plant listed in column P on the element for the given contingency
The colors in columns F-Q represent the CM Zone of the respective plant:
West
North
South
Houston
*On the W-N sheet Willow Creek-Jacksboro was defined in the N-W direction, thus the PTDF is negative instead of positive

## N-S PTDFs
Contingency # | Element | Contingency | PTDF | Top 3 plants with the highest impact in each direction
base case | CSC_3 | Base Case | 36
base case | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Base Case | 3.1 | Clipper Silver Star | 3.5241 | Calahan Divide | 3.3655 | Buffalo Gap | 3.1756 | Buchanan | -8.8643 | Inks | -8.0387 | Wirtz | -6.2892
base case | THOUSE__5_LAKE_CRK1_5_345_Line | Base Case | 6.7 | Tradinghouse | 18.4092 | Bosque | 12.5769 | Whitney | 7.1718 | Lake Creek | -13.1195 | Sandow | -3.5831 | Lost Pines | -3.3288
base case | LAKE_CRK1_5_TEMP_SS__5_345_Line | Base Case | 19.9 | Tradinghouse | 14.1672 | Lake Creek | 12.7934 | Bosque | 12.1025 | Sandow | -17.9481 | Bastrop Energy | -14.5885 | Lost Pines | -14.5492
base case | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Base Case | 2.6 | Lake Creek | 8.2594 | Bosque | 1.7626 | Whitney | 1.4795 | Sandow | -2.3693 | Decker | -1.9499 | Lake Austin | -1.9413
base case | THOUSE__5_TEMP_PEC__5_345_Line | Base Case | 17.7 | Tradinghouse | 15.9709 | Bosque | 12.6614 | Midlothian | 9.5794 | Sandow | -15.353 | Decker | -12.449 | Bastrop Energy | -12.4361
base case | TEMP_PEC__5_TEMP_SS__5_345_Line | Base Case | 17 | Tradinghouse | 13.9608 | Bosque | 12.6521 | Lake Creek | 10.7993 | Sandow | -14.8057 | Lost Pines | -13.0013 | Bastrop Energy | -12.9133
base case | TEMP_SS__8_ROGERS1A_8_138_Line | Base Case | 2.3 | Lake Creek | 2.132 | Bosque | 1.9614 | Whitney | 1.8183 | Sandow | -8.1228 | Sim Gideon | -1.9554 | Decker | -1.7652
base case | TEMP_PEC__8_TEMP_SS__8_138_Line | Base Case | 2.8 | Lake Creek | 3.7081 | Tradinghouse | 2.2107 | Bosque | 1.9761 | Sandow | -3.0425 | Marshall Ford | -2.5734 | Lake Austin | -2.5248
base case | SANDOW1_8_ELGIN_SS__8_138_Line | Base Case | 2.6 | Sandow | 8.2808 | Tradinghouse | 1.3385 | Lake Creek | 1.3199 | Sim Gideon | -5.2666 | Lake Austin | -3.6825 | Decker | -3.6219
base case | SANDOW1_8_SALTY_P_8_138_Line | Base Case | 2.6 | Sandow | 8.3251 | Tradinghouse | 1.3761 | Lake Creek | 1.3662 | Lake Austin | -4.1063 | Marshall Ford | -3.9445 | Decker | -3.891
base case | SANDOW__5_L_AUSTRO5_1Y_345_Line | Base Case | 18 | Sandow | 17.0151 | Tradinghouse | 11.773 | Lake Creek | 11.749 | Lost Pines | -16.602 | Bastrop Energy | -16.1656 | Fayette | -14.1226
base case | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Base Case | 9.5 | Lost Pines | 12.3895 | Sandow | 10.3385 | Bastrop Energy | 8.8308 | Hays | -20.4541 | Rio Nogales | -18.6271 | Guadalupe Power Partners | -17.0048
base case | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Base Case | 12.1 | Lost Pines | 14.5135 | Sandow | 11.9525 | Tradinghouse | 8.2544 | Bastrop Energy | -56.0367 | Sandhill | -15.8673 | Lake Austin | -12.2862
base case | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Base Case | 17.8 | Sandow | 17.1204 | Tradinghouse | 11.695 | Lake Creek | 11.6732 | Lost Pines | -16.5139 | Bastrop Energy | -16.0784 | Fayette | -14.0456
base case | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Base Case | 2.7 | Clipper Silver Star | 3.025 | Calahan Divide | 2.8873 | Horse Hollow | 2.7226 | Buchanan | -7.7265 | Inks | -7.0101 | Wirtz | -5.4917
base case | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Base Case | 2.7 | Clipper Silver Star | 3.0326 | Calahan Divide | 2.895 | Horse Hollow | 2.7302 | Buchanan | -7.7189 | Inks | -7.0024 | Wirtz | -5.4841
base case | ROGERS1A_8_SANDOW1_8_138_Line | Base Case | 2.3 | Lake Creek | 2.1266 | Bosque | 1.956 | Whitney | 1.8129 | Sandow | -8.1281 | Sim Gideon | -1.9608 | Decker | -1.7706
base case | THOUSE__5_LAKE_CRK2_5_345_Line | Base Case | 7.9 | Tradinghouse | 21.7611 | Bosque | 14.7694 | Whitney | 8.3597 | Lake Creek | -16.395 | Sandow | -4.2245 | Lost Pines | -3.9169
1 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 3.9 | Clipper Silver Star | 3.8942 | Calahan Divide | 3.684 | Horse Hollow | 3.4955 | Buchanan | -9.1555 | Inks | -8.3332 | Wirtz | -6.6543
1 | THOUSE__5_LAKE_CRK1_5_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 5.9 | Tradinghouse | 17.8195 | Bosque | 12.0141 | Whitney | 6.6731 | Lake Creek | -13.6942 | TH Wharton | -2.8718 | Sandow | -2.8215
1 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 8.3 | Tradinghouse | 5.8776 | Lake Creek | 4.7148 | Midlothian | 4.2854 | Buchanan | -8.009 | Inks | -7.5002 | Sandow | -7.2416
1 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 2.1 | Lake Creek | 7.8752 | Bosque | 1.3864 | Whitney | 1.1461 | Sandow | -1.8601 | Buchanan | -1.7202 | Inks | -1.624
1 | THOUSE__5_TEMP_PEC__5_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 9 | Tradinghouse | 9.7464 | Bosque | 6.721 | Midlothian | 5.3381 | Buchanan | -7.5197 | Sandow | -7.3139 | Inks | -7.0532
1 | TEMP_PEC__5_TEMP_SS__5_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 2.8 | Tradinghouse | 3.7583 | Bosque | 2.9151 | Whitney | 1.8902 | Buchanan | -3.4468 | Inks | -3.1823 | Wirtz | -2.7195
1 | TEMP_SS__8_ROGERS1A_8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 9.3 | Lake Creek | 7.0242 | Tradinghouse | 6.6887 | Bosque | 6.6103 | Sandow | -14.6064 | Lost Pines | -7.4483 | Bastrop Energy | -7.3815
1 | TEMP_PEC__8_TEMP_SS__8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 5.9 | Lake Creek | 5.872 | Tradinghouse | 4.4312 | Bosque | 4.0952 | Sandow | -5.9103 | Decker | -4.6661 | Lake Austin | -4.6503
1 | SANDOW1_8_ELGIN_SS__8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 1.4 | Sandow | 9.3778 | Dansby | 1.1091 | Atkins | 0.9801 | Sim Gideon | -4.428 | Lake Austin | -2.8694 | Marshall Ford | -2.7748
1 | SANDOW1_8_SALTY_P_8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 1.4 | Sandow | 9.4354 | Dansby | 1.1654 | Atkins | 1.0364 | Lake Austin | -3.2833 | Marshall Ford | -3.2143 | Decker | -3.0335
1 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 6 | Sandow | 28.1228 | Lake Creek | 3.3676 | Dansby | 3.2481 | Lost Pines | -6.8238 | Bastrop Energy | -6.4963 | Fayette | -5.583
1 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 4.5 | Lost Pines | 16.4994 | Sandow | 15.0072 | Bastrop Energy | 12.8949 | Hays | -17.0274 | Rio Nogales | -15.3592 | Guadalupe Power Partners | -13.885
1 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 3.9 | Lost Pines | 21.187 | Sandow | 19.5333 | Sim Gideon | 4.6674 | Bastrop Energy | -49.4375 | Sandhill | -10.0654 | Lake Austin | -6.6676
1 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 6 | Sandow | 28.1239 | Lake Creek | 3.3704 | Dansby | 3.2489 | Lost Pines | -6.8274 | Bastrop Energy | -6.4999 | Fayette | -5.5861
1 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 3.4 | Clipper Silver Star | 3.3462 | Calahan Divide | 3.1638 | Buffalo Gap | 3.0002 | Buchanan | -7.9792 | Inks | -7.2656 | Wirtz | -5.8086
1 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 3.4 | Clipper Silver Star | 3.3538 | Calahan Divide | 3.1714 | Buffalo Gap | 3.0078 | Buchanan | -7.9716 | Inks | -7.258 | Wirtz | -5.8009
1 | ROGERS1A_8_SANDOW1_8_138_Line | Temple-Sandow double circuit 345-kV line [CSC] | 9.3 | Lake Creek | 7.0189 | Tradinghouse | 6.6834 | Bosque | 6.6049 | Sandow | -14.6117 | Lost Pines | -7.4536 | Bastrop Energy | -7.3868
1 | THOUSE__5_LAKE_CRK2_5_345_Line | Temple-Sandow double circuit 345-kV line [CSC] | 7 | Tradinghouse | 21.08 | Bosque | 14.1193 | Whitney | 7.7837 | Lake Creek | -17.0588 | TH Wharton | -3.3731 | Sandow | -3.3448
2 | CSC_3 | Brownwood-Goldthwaite 138-kV line | 36.7
2 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Brownwood-Goldthwaite 138-kV line | 0
2 | THOUSE__5_LAKE_CRK1_5_345_Line | Brownwood-Goldthwaite 138-kV line | 7
2 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Brownwood-Goldthwaite 138-kV line | 20.7
2 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.7
2 | THOUSE__5_TEMP_PEC__5_345_Line | Brownwood-Goldthwaite 138-kV line | 18.4
2 | TEMP_PEC__5_TEMP_SS__5_345_Line | Brownwood-Goldthwaite 138-kV line | 17.6
2 | TEMP_SS__8_ROGERS1A_8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.3
2 | TEMP_PEC__8_TEMP_SS__8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.9
2 | SANDOW1_8_ELGIN_SS__8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.7
2 | SANDOW1_8_SALTY_P_8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.7
2 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Brownwood-Goldthwaite 138-kV line | 18.3
2 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Brownwood-Goldthwaite 138-kV line | 9.6
2 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Brownwood-Goldthwaite 138-kV line | 12.4
2 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Brownwood-Goldthwaite 138-kV line | 18.2
2 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Brownwood-Goldthwaite 138-kV line | 0
2 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Brownwood-Goldthwaite 138-kV line | 0
2 | ROGERS1A_8_SANDOW1_8_138_Line | Brownwood-Goldthwaite 138-kV line | 2.3
2 | THOUSE__5_LAKE_CRK2_5_345_Line | Brownwood-Goldthwaite 138-kV line | 8.2
3 | CSC_3 | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 36
3 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 3.1
3 | THOUSE__5_LAKE_CRK1_5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 0
3 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 19.3
3 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.6
3 | THOUSE__5_TEMP_PEC__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 18.3
3 | TEMP_PEC__5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 17.5
3 | TEMP_SS__8_ROGERS1A_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.3
3 | TEMP_PEC__8_TEMP_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.8
3 | SANDOW1_8_ELGIN_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.6
3 | SANDOW1_8_SALTY_P_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.6
3 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 17.9
3 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 9.5
3 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 12.1
3 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 17.8
3 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.7
3 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.7
3 | ROGERS1A_8_SANDOW1_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 2.3
3 | THOUSE__5_LAKE_CRK2_5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 13.3
4 | CSC_3 | Lake Creek-Temple 345-kV line | 31.9
4 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Lake Creek-Temple 345-kV line | 3.4
4 | THOUSE__5_LAKE_CRK1_5_345_Line | Lake Creek-Temple 345-kV line | 0.1
4 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Lake Creek-Temple 345-kV line | 0
4 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Lake Creek-Temple 345-kV line | 4.2
4 | THOUSE__5_TEMP_PEC__5_345_Line | Lake Creek-Temple 345-kV line | 29.4
4 | TEMP_PEC__5_TEMP_SS__5_345_Line | Lake Creek-Temple 345-kV line | 30.1
4 | TEMP_SS__8_ROGERS1A_8_138_Line | Lake Creek-Temple 345-kV line | 2.3
4 | TEMP_PEC__8_TEMP_SS__8_138_Line | Lake Creek-Temple 345-kV line | 3.4
4 | SANDOW1_8_ELGIN_SS__8_138_Line | Lake Creek-Temple 345-kV line | 2.4
4 | SANDOW1_8_SALTY_P_8_138_Line | Lake Creek-Temple 345-kV line | 2.5
4 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple 345-kV line | 16.3
4 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Lake Creek-Temple 345-kV line | 8.7
4 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Lake Creek-Temple 345-kV line | 11
4 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple 345-kV line | 16.2
4 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Lake Creek-Temple 345-kV line | 3
4 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Lake Creek-Temple 345-kV line | 3
4 | ROGERS1A_8_SANDOW1_8_138_Line | Lake Creek-Temple 345-kV line | 2.3
4 | THOUSE__5_LAKE_CRK2_5_345_Line | Lake Creek-Temple 345-kV line | 0.2
5 | CSC_3 | Lake Creek-Temple Pecan 138-kV line | 35.9
5 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Lake Creek-Temple Pecan 138-kV line | 3.1
5 | THOUSE__5_LAKE_CRK1_5_345_Line | Lake Creek-Temple Pecan 138-kV line | 6.4
5 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Lake Creek-Temple Pecan 138-kV line | 20.8
5 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Lake Creek-Temple Pecan 138-kV line | 0
5 | THOUSE__5_TEMP_PEC__5_345_Line | Lake Creek-Temple Pecan 138-kV line | 18.5
5 | TEMP_PEC__5_TEMP_SS__5_345_Line | Lake Creek-Temple Pecan 138-kV line | 16.6
5 | TEMP_SS__8_ROGERS1A_8_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.2
5 | TEMP_PEC__8_TEMP_SS__8_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.2
5 | SANDOW1_8_ELGIN_SS__8_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.6
5 | SANDOW1_8_SALTY_P_8_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.6
5 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple Pecan 138-kV line | 17.9
5 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Lake Creek-Temple Pecan 138-kV line | 9.5
5 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Lake Creek-Temple Pecan 138-kV line | 12.1
5 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple Pecan 138-kV line | 17.8
5 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.7
5 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.7
5 | ROGERS1A_8_SANDOW1_8_138_Line | Lake Creek-Temple Pecan 138-kV line | 2.2
5 | THOUSE__5_LAKE_CRK2_5_345_Line | Lake Creek-Temple Pecan 138-kV line | 7.5
6 | CSC_3 | Tradinghouse-Temple Pecan 345-kV line | 33.1
6 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Tradinghouse-Temple Pecan 345-kV line | 3.4
6 | THOUSE__5_LAKE_CRK1_5_345_Line | Tradinghouse-Temple Pecan 345-kV line | 13
6 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Tradinghouse-Temple Pecan 345-kV line | 30.9
6 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 4
6 | THOUSE__5_TEMP_PEC__5_345_Line | Tradinghouse-Temple Pecan 345-kV line | 0
6 | TEMP_PEC__5_TEMP_SS__5_345_Line | Tradinghouse-Temple Pecan 345-kV line | 2.2
6 | TEMP_SS__8_ROGERS1A_8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.2
6 | TEMP_PEC__8_TEMP_SS__8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.4
6 | SANDOW1_8_ELGIN_SS__8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.5
6 | SANDOW1_8_SALTY_P_8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.5
6 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Temple Pecan 345-kV line | 16.8
6 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Tradinghouse-Temple Pecan 345-kV line | 8.9
6 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Tradinghouse-Temple Pecan 345-kV line | 11.3
6 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Temple Pecan 345-kV line | 16.7
6 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.9
6 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.9
6 | ROGERS1A_8_SANDOW1_8_138_Line | Tradinghouse-Temple Pecan 345-kV line | 2.2
6 | THOUSE__5_LAKE_CRK2_5_345_Line | Tradinghouse-Temple Pecan 345-kV line | 15.4
7 | CSC_3 | Temple Pecan-Temple 345-kV line | 32.9
7 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Temple Pecan-Temple 345-kV line | 3.3
7 | THOUSE__5_LAKE_CRK1_5_345_Line | Temple Pecan-Temple 345-kV line | 10.4
7 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Temple Pecan-Temple 345-kV line | 27.9
7 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Temple Pecan-Temple 345-kV line | 2.2
7 | THOUSE__5_TEMP_PEC__5_345_Line | Temple Pecan-Temple 345-kV line | 7.9
7 | TEMP_PEC__5_TEMP_SS__5_345_Line | Temple Pecan-Temple 345-kV line | 0
7 | TEMP_SS__8_ROGERS1A_8_138_Line | Temple Pecan-Temple 345-kV line | 2.9
7 | TEMP_PEC__8_TEMP_SS__8_138_Line | Temple Pecan-Temple 345-kV line | 6.6
7 | SANDOW1_8_ELGIN_SS__8_138_Line | Temple Pecan-Temple 345-kV line | 2.5
7 | SANDOW1_8_SALTY_P_8_138_Line | Temple Pecan-Temple 345-kV line | 2.5
7 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 345-kV line | 16.9
7 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Temple Pecan-Temple 345-kV line | 9.1
7 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Temple Pecan-Temple 345-kV line | 11.4
7 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 345-kV line | 16.8
7 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Temple Pecan-Temple 345-kV line | 2.8
7 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Temple Pecan-Temple 345-kV line | 2.8
7 | ROGERS1A_8_SANDOW1_8_138_Line | Temple Pecan-Temple 345-kV line | 2.9
7 | THOUSE__5_LAKE_CRK2_5_345_Line | Temple Pecan-Temple 345-kV line | 12.3
8 | CSC_3 | Temple-Rogers 138-kV line | 37.6
8 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Temple-Rogers 138-kV line | 3.1
8 | THOUSE__5_LAKE_CRK1_5_345_Line | Temple-Rogers 138-kV line | 6.7
8 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Temple-Rogers 138-kV line | 19.9
8 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Temple-Rogers 138-kV line | 2.5
8 | THOUSE__5_TEMP_PEC__5_345_Line | Temple-Rogers 138-kV line | 17.6
8 | TEMP_PEC__5_TEMP_SS__5_345_Line | Temple-Rogers 138-kV line | 17.6
8 | TEMP_SS__8_ROGERS1A_8_138_Line | Temple-Rogers 138-kV line | 0
8 | TEMP_PEC__8_TEMP_SS__8_138_Line | Temple-Rogers 138-kV line | 2.2
8 | SANDOW1_8_ELGIN_SS__8_138_Line | Temple-Rogers 138-kV line | 2.4
8 | SANDOW1_8_SALTY_P_8_138_Line | Temple-Rogers 138-kV line | 2.5
8 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Temple-Rogers 138-kV line | 17.9
8 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Temple-Rogers 138-kV line | 9.5
8 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Temple-Rogers 138-kV line | 12
8 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Temple-Rogers 138-kV line | 17.7
8 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Temple-Rogers 138-kV line | 2.7
8 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Temple-Rogers 138-kV line | 2.7
8 | ROGERS1A_8_SANDOW1_8_138_Line | Temple-Rogers 138-kV line | 0
8 | THOUSE__5_LAKE_CRK2_5_345_Line | Temple-Rogers 138-kV line | 7.9
9 | CSC_3 | Temple Pecan-Temple 138-kV line | 36.1
9 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Temple Pecan-Temple 138-kV line | 3.1
9 | THOUSE__5_LAKE_CRK1_5_345_Line | Temple Pecan-Temple 138-kV line | 6.7
9 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Temple Pecan-Temple 138-kV line | 20
9 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Temple Pecan-Temple 138-kV line | 2.4
9 | THOUSE__5_TEMP_PEC__5_345_Line | Temple Pecan-Temple 138-kV line | 17.6
9 | TEMP_PEC__5_TEMP_SS__5_345_Line | Temple Pecan-Temple 138-kV line | 17.9
9 | TEMP_SS__8_ROGERS1A_8_138_Line | Temple Pecan-Temple 138-kV line | 2.2
9 | TEMP_PEC__8_TEMP_SS__8_138_Line | Temple Pecan-Temple 138-kV line | 0
9 | SANDOW1_8_ELGIN_SS__8_138_Line | Temple Pecan-Temple 138-kV line | 2.6
9 | SANDOW1_8_SALTY_P_8_138_Line | Temple Pecan-Temple 138-kV line | 2.6
9 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 138-kV line | 18
9 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Temple Pecan-Temple 138-kV line | 9.5
9 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Temple Pecan-Temple 138-kV line | 12.1
9 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 138-kV line | 17.9
9 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Temple Pecan-Temple 138-kV line | 2.7
9 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Temple Pecan-Temple 138-kV line | 2.7
9 | ROGERS1A_8_SANDOW1_8_138_Line | Temple Pecan-Temple 138-kV line | 2.2
9 | THOUSE__5_LAKE_CRK2_5_345_Line | Temple Pecan-Temple 138-kV line | 7.9
10 | CSC_3 | Sandow-Elgin 138-kV line | 35.7
10 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Sandow-Elgin 138-kV line | 3.1
10 | THOUSE__5_LAKE_CRK1_5_345_Line | Sandow-Elgin 138-kV line | 6.7
10 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Sandow-Elgin 138-kV line | 19.8
10 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Sandow-Elgin 138-kV line | 2.6
10 | THOUSE__5_TEMP_PEC__5_345_Line | Sandow-Elgin 138-kV line | 17.6
10 | TEMP_PEC__5_TEMP_SS__5_345_Line | Sandow-Elgin 138-kV line | 16.9
10 | TEMP_SS__8_ROGERS1A_8_138_Line | Sandow-Elgin 138-kV line | 2.2
10 | TEMP_PEC__8_TEMP_SS__8_138_Line | Sandow-Elgin 138-kV line | 2.8
10 | SANDOW1_8_ELGIN_SS__8_138_Line | Sandow-Elgin 138-kV line | 0
10 | SANDOW1_8_SALTY_P_8_138_Line | Sandow-Elgin 138-kV line | 3.4
10 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Sandow-Elgin 138-kV line | 18.6
10 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Sandow-Elgin 138-kV line | 9.6
10 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Sandow-Elgin 138-kV line | 12.5
10 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Sandow-Elgin 138-kV line | 18.5
10 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Sandow-Elgin 138-kV line | 2.7
10 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Sandow-Elgin 138-kV line | 2.7
10 | ROGERS1A_8_SANDOW1_8_138_Line | Sandow-Elgin 138-kV line | 2.2
10 | THOUSE__5_LAKE_CRK2_5_345_Line | Sandow-Elgin 138-kV line | 7.9
11 | CSC_3 | Sandow-Salty 138-kV line | 35.7
11 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Sandow-Salty 138-kV line | 3.1
11 | THOUSE__5_LAKE_CRK1_5_345_Line | Sandow-Salty 138-kV line | 6.7
11 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Sandow-Salty 138-kV line | 19.8
11 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Sandow-Salty 138-kV line | 2.6
11 | THOUSE__5_TEMP_PEC__5_345_Line | Sandow-Salty 138-kV line | 17.6
11 | TEMP_PEC__5_TEMP_SS__5_345_Line | Sandow-Salty 138-kV line | 16.9
11 | TEMP_SS__8_ROGERS1A_8_138_Line | Sandow-Salty 138-kV line | 2.1
11 | TEMP_PEC__8_TEMP_SS__8_138_Line | Sandow-Salty 138-kV line | 2.8
11 | SANDOW1_8_ELGIN_SS__8_138_Line | Sandow-Salty 138-kV line | 3.4
11 | SANDOW1_8_SALTY_P_8_138_Line | Sandow-Salty 138-kV line | 0
11 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Sandow-Salty 138-kV line | 18.6
11 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Sandow-Salty 138-kV line | 9.6
11 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Sandow-Salty 138-kV line | 12.6
11 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Sandow-Salty 138-kV line | 18.5
11 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Sandow-Salty 138-kV line | 2.7
11 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Sandow-Salty 138-kV line | 2.7
11 | ROGERS1A_8_SANDOW1_8_138_Line | Sandow-Salty 138-kV line | 2.1
11 | THOUSE__5_LAKE_CRK2_5_345_Line | Sandow-Salty 138-kV line | 7.9
12 | CSC_3 | Sandow-Austrop 345-kV line, ckt 1 | 32.3
12 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 3.2
12 | THOUSE__5_LAKE_CRK1_5_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 6.6
12 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 18.5
12 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.5
12 | THOUSE__5_TEMP_PEC__5_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 16.6
12 | TEMP_PEC__5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 15.6
12 | TEMP_SS__8_ROGERS1A_8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.2
12 | TEMP_PEC__8_TEMP_SS__8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.9
12 | SANDOW1_8_ELGIN_SS__8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 3.4
12 | SANDOW1_8_SALTY_P_8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 3.5
12 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 0
12 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 8.5
12 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 10.2
12 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 30.1
12 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.8
12 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.8
12 | ROGERS1A_8_SANDOW1_8_138_Line | Sandow-Austrop 345-kV line, ckt 1 | 2.2
12 | THOUSE__5_LAKE_CRK2_5_345_Line | Sandow-Austrop 345-kV line, ckt 1 | 7.8
13 | CSC_3 | Austrop-Zorn 345-kV line | 35
13 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Austrop-Zorn 345-kV line | 3.1
13 | THOUSE__5_LAKE_CRK1_5_345_Line | Austrop-Zorn 345-kV line | 6.7
13 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Austrop-Zorn 345-kV line | 19.5
13 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Austrop-Zorn 345-kV line | 2.6
13 | THOUSE__5_TEMP_PEC__5_345_Line | Austrop-Zorn 345-kV line | 17.3
13 | TEMP_PEC__5_TEMP_SS__5_345_Line | Austrop-Zorn 345-kV line | 16.6
13 | TEMP_SS__8_ROGERS1A_8_138_Line | Austrop-Zorn 345-kV line | 2.3
13 | TEMP_PEC__8_TEMP_SS__8_138_Line | Austrop-Zorn 345-kV line | 2.8
13 | SANDOW1_8_ELGIN_SS__8_138_Line | Austrop-Zorn 345-kV line | 2.7
13 | SANDOW1_8_SALTY_P_8_138_Line | Austrop-Zorn 345-kV line | 2.7
13 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Austrop-Zorn 345-kV line | 17.3
13 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Austrop-Zorn 345-kV line | 0
13 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Austrop-Zorn 345-kV line | 17.1
13 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Austrop-Zorn 345-kV line | 17.2
13 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Austrop-Zorn 345-kV line | 2.7
13 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Austrop-Zorn 345-kV line | 2.7
13 | ROGERS1A_8_SANDOW1_8_138_Line | Austrop-Zorn 345-kV line | 2.3
13 | THOUSE__5_LAKE_CRK2_5_345_Line | Austrop-Zorn 345-kV line | 7.9
14 | CSC_3 | Austrop-Garfield 345-kV line | 34.9
14 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Austrop-Garfield 345-kV line | 3.2
14 | THOUSE__5_LAKE_CRK1_5_345_Line | Austrop-Garfield 345-kV line | 6.7
14 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Austrop-Garfield 345-kV line | 19.5
14 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Austrop-Garfield 345-kV line | 2.6
14 | THOUSE__5_TEMP_PEC__5_345_Line | Austrop-Garfield 345-kV line | 17.3
14 | TEMP_PEC__5_TEMP_SS__5_345_Line | Austrop-Garfield 345-kV line | 16.6
14 | TEMP_SS__8_ROGERS1A_8_138_Line | Austrop-Garfield 345-kV line | 2.3
14 | TEMP_PEC__8_TEMP_SS__8_138_Line | Austrop-Garfield 345-kV line | 2.9
14 | SANDOW1_8_ELGIN_SS__8_138_Line | Austrop-Garfield 345-kV line | 2.8
14 | SANDOW1_8_SALTY_P_8_138_Line | Austrop-Garfield 345-kV line | 2.9
14 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Austrop-Garfield 345-kV line | 17.1
14 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Austrop-Garfield 345-kV line | 13.1
14 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Austrop-Garfield 345-kV line | 0
14 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Austrop-Garfield 345-kV line | 17
14 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Austrop-Garfield 345-kV line | 2.7
14 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Austrop-Garfield 345-kV line | 2.7
14 | ROGERS1A_8_SANDOW1_8_138_Line | Austrop-Garfield 345-kV line | 2.3
14 | THOUSE__5_LAKE_CRK2_5_345_Line | Austrop-Garfield 345-kV line | 7.9
15 | CSC_3 | Sandow-Austrop 345-kV line, ckt 2 | 32.4
15 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 3.2
15 | THOUSE__5_LAKE_CRK1_5_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 6.6
15 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 18.5
15 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.5
15 | THOUSE__5_TEMP_PEC__5_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 16.6
15 | TEMP_PEC__5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 15.6
15 | TEMP_SS__8_ROGERS1A_8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.2
15 | TEMP_PEC__8_TEMP_SS__8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.9
15 | SANDOW1_8_ELGIN_SS__8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 3.4
15 | SANDOW1_8_SALTY_P_8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 3.5
15 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 30.1
15 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 8.5
15 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 10.2
15 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 0
15 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.8
15 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.8
15 | ROGERS1A_8_SANDOW1_8_138_Line | Sandow-Austrop 345-kV line, ckt 2 | 2.2
15 | THOUSE__5_LAKE_CRK2_5_345_Line | Sandow-Austrop 345-kV line, ckt 2 | 7.8
16 | CSC_3 | Evant-Adamsville 138-kV line | 36.5
16 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Evant-Adamsville 138-kV line | 0.9
16 | THOUSE__5_LAKE_CRK1_5_345_Line | Evant-Adamsville 138-kV line | 6.9
16 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Evant-Adamsville 138-kV line | 20.4
16 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Evant-Adamsville 138-kV line | 2.7
16 | THOUSE__5_TEMP_PEC__5_345_Line | Evant-Adamsville 138-kV line | 18.2
16 | TEMP_PEC__5_TEMP_SS__5_345_Line | Evant-Adamsville 138-kV line | 17.4
16 | TEMP_SS__8_ROGERS1A_8_138_Line | Evant-Adamsville 138-kV line | 2.3
16 | TEMP_PEC__8_TEMP_SS__8_138_Line | Evant-Adamsville 138-kV line | 2.9
16 | SANDOW1_8_ELGIN_SS__8_138_Line | Evant-Adamsville 138-kV line | 2.6
16 | SANDOW1_8_SALTY_P_8_138_Line | Evant-Adamsville 138-kV line | 2.7
16 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Evant-Adamsville 138-kV line | 18.2
16 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Evant-Adamsville 138-kV line | 9.6
16 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Evant-Adamsville 138-kV line | 12.3
16 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Evant-Adamsville 138-kV line | 18.1
16 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Evant-Adamsville 138-kV line | 0
16 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Evant-Adamsville 138-kV line | 0
16 | ROGERS1A_8_SANDOW1_8_138_Line | Evant-Adamsville 138-kV line | 2.3
16 | THOUSE__5_LAKE_CRK2_5_345_Line | Evant-Adamsville 138-kV line | 8.1
17 | CSC_3 | Goldthwaite-Evant 138-kV line | 36.5
17 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Goldthwaite-Evant 138-kV line | 0.9
17 | THOUSE__5_LAKE_CRK1_5_345_Line | Goldthwaite-Evant 138-kV line | 6.9
17 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Goldthwaite-Evant 138-kV line | 20.4
17 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Goldthwaite-Evant 138-kV line | 2.7
17 | THOUSE__5_TEMP_PEC__5_345_Line | Goldthwaite-Evant 138-kV line | 18.2
17 | TEMP_PEC__5_TEMP_SS__5_345_Line | Goldthwaite-Evant 138-kV line | 17.4
17 | TEMP_SS__8_ROGERS1A_8_138_Line | Goldthwaite-Evant 138-kV line | 2.3
17 | TEMP_PEC__8_TEMP_SS__8_138_Line | Goldthwaite-Evant 138-kV line | 2.9
17 | SANDOW1_8_ELGIN_SS__8_138_Line | Goldthwaite-Evant 138-kV line | 2.6
17 | SANDOW1_8_SALTY_P_8_138_Line | Goldthwaite-Evant 138-kV line | 2.7
17 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Goldthwaite-Evant 138-kV line | 18.2
17 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Goldthwaite-Evant 138-kV line | 9.6
17 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Goldthwaite-Evant 138-kV line | 12.3
17 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Goldthwaite-Evant 138-kV line | 18.1
17 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Goldthwaite-Evant 138-kV line | 0
17 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Goldthwaite-Evant 138-kV line | 0
17 | ROGERS1A_8_SANDOW1_8_138_Line | Goldthwaite-Evant 138-kV line | 2.3
17 | THOUSE__5_LAKE_CRK2_5_345_Line | Goldthwaite-Evant 138-kV line | 8.1
18 | CSC_3 | Rogers-Sandow 138-kV line | 37.6
18 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Rogers-Sandow 138-kV line | 3.1
18 | THOUSE__5_LAKE_CRK1_5_345_Line | Rogers-Sandow 138-kV line | 6.7
18 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Rogers-Sandow 138-kV line | 19.9
18 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Rogers-Sandow 138-kV line | 2.5
18 | THOUSE__5_TEMP_PEC__5_345_Line | Rogers-Sandow 138-kV line | 17.6
18 | TEMP_PEC__5_TEMP_SS__5_345_Line | Rogers-Sandow 138-kV line | 17.6
18 | TEMP_SS__8_ROGERS1A_8_138_Line | Rogers-Sandow 138-kV line | 0
18 | TEMP_PEC__8_TEMP_SS__8_138_Line | Rogers-Sandow 138-kV line | 2.2
18 | SANDOW1_8_ELGIN_SS__8_138_Line | Rogers-Sandow 138-kV line | 2.4
18 | SANDOW1_8_SALTY_P_8_138_Line | Rogers-Sandow 138-kV line | 2.5
18 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Rogers-Sandow 138-kV line | 17.9
18 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Rogers-Sandow 138-kV line | 9.5
18 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Rogers-Sandow 138-kV line | 12
18 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Rogers-Sandow 138-kV line | 17.7
18 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Rogers-Sandow 138-kV line | 2.7
18 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Rogers-Sandow 138-kV line | 2.7
18 | ROGERS1A_8_SANDOW1_8_138_Line | Rogers-Sandow 138-kV line | 0
18 | THOUSE__5_LAKE_CRK2_5_345_Line | Rogers-Sandow 138-kV line | 7.9
19 | CSC_3 | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 35.9
19 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 3.1
19 | THOUSE__5_LAKE_CRK1_5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 12.8
19 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 19.1
19 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.5
19 | THOUSE__5_TEMP_PEC__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 18.5
19 | TEMP_PEC__5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 17.7
19 | TEMP_SS__8_ROGERS1A_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.3
19 | TEMP_PEC__8_TEMP_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.8
19 | SANDOW1_8_ELGIN_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.6
19 | SANDOW1_8_SALTY_P_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.6
19 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 17.9
19 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 9.5
19 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 12.1
19 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 17.8
19 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.7
19 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.7
19 | ROGERS1A_8_SANDOW1_8_138_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 2.3
19 | THOUSE__5_LAKE_CRK2_5_345_Line | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 0
20 | CSC_3 | Tradinghouse-Lake Creek 345-kV double circuit | 32.8
20 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 3.4
20 | THOUSE__5_LAKE_CRK1_5_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 0
20 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 30.4
20 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 4
20 | THOUSE__5_TEMP_PEC__5_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 0
20 | TEMP_PEC__5_TEMP_SS__5_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.3
20 | TEMP_SS__8_ROGERS1A_8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.2
20 | TEMP_PEC__8_TEMP_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.4
20 | SANDOW1_8_ELGIN_SS__8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.5
20 | SANDOW1_8_SALTY_P_8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.5
20 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 16.7
20 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 8.9
20 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 11.3
20 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 16.6
20 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 3
20 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 3
20 | ROGERS1A_8_SANDOW1_8_138_Line | Tradinghouse-Lake Creek 345-kV double circuit | 2.2
20 | THOUSE__5_LAKE_CRK2_5_345_Line | Tradinghouse-Lake Creek 345-kV double circuit | 26.7
21 | CSC_3 | Lake Creek-Temple Pecan 345-kV double circuit | 18.3
21 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 4.5
21 | THOUSE__5_LAKE_CRK1_5_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 7.1
21 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 0
21 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 10.2
21 | THOUSE__5_TEMP_PEC__5_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 0
21 | TEMP_PEC__5_TEMP_SS__5_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 10
21 | TEMP_SS__8_ROGERS1A_8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 2
21 | TEMP_PEC__8_TEMP_SS__8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 3.2
21 | SANDOW1_8_ELGIN_SS__8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 1.9
21 | SANDOW1_8_SALTY_P_8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 2
21 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 10.8
21 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 6
21 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 7.3
21 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 10.7
21 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 3.9
21 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 3.9
21 | ROGERS1A_8_SANDOW1_8_138_Line | Lake Creek-Temple Pecan 345-kV double circuit | 2
21 | THOUSE__5_LAKE_CRK2_5_345_Line | Lake Creek-Temple Pecan 345-kV double circuit | 8.6
22 | CSC_3 | Temple Pecan-Temple 345-kV double circuit | 18.3
22 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Temple Pecan-Temple 345-kV double circuit | 4.5
22 | THOUSE__5_LAKE_CRK1_5_345_Line | Temple Pecan-Temple 345-kV double circuit | 7.1
22 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Temple Pecan-Temple 345-kV double circuit | 0
22 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Temple Pecan-Temple 345-kV double circuit | 10.2
22 | THOUSE__5_TEMP_PEC__5_345_Line | Temple Pecan-Temple 345-kV double circuit | 0
22 | TEMP_PEC__5_TEMP_SS__5_345_Line | Temple Pecan-Temple 345-kV double circuit | 10
22 | TEMP_SS__8_ROGERS1A_8_138_Line | Temple Pecan-Temple 345-kV double circuit | 2
22 | TEMP_PEC__8_TEMP_SS__8_138_Line | Temple Pecan-Temple 345-kV double circuit | 3.2
22 | SANDOW1_8_ELGIN_SS__8_138_Line | Temple Pecan-Temple 345-kV double circuit | 1.9
22 | SANDOW1_8_SALTY_P_8_138_Line | Temple Pecan-Temple 345-kV double circuit | 2
22 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 345-kV double circuit | 10.8
22 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Temple Pecan-Temple 345-kV double circuit | 6
22 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Temple Pecan-Temple 345-kV double circuit | 7.3
22 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Temple Pecan-Temple 345-kV double circuit | 10.7
22 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Temple Pecan-Temple 345-kV double circuit | 3.9
22 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Temple Pecan-Temple 345-kV double circuit | 3.9
22 | ROGERS1A_8_SANDOW1_8_138_Line | Temple Pecan-Temple 345-kV double circuit | 2
22 | THOUSE__5_LAKE_CRK2_5_345_Line | Temple Pecan-Temple 345-kV double circuit | 8.6
23 | CSC_3 | Sandow-Austrop 345-kV double circuit | 13.3
23 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Sandow-Austrop 345-kV double circuit | 3.8
23 | THOUSE__5_LAKE_CRK1_5_345_Line | Sandow-Austrop 345-kV double circuit | 6.1
23 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV double circuit | 11.1
23 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Sandow-Austrop 345-kV double circuit | 1.9
23 | THOUSE__5_TEMP_PEC__5_345_Line | Sandow-Austrop 345-kV double circuit | 10.8
23 | TEMP_PEC__5_TEMP_SS__5_345_Line | Sandow-Austrop 345-kV double circuit | 7.9
23 | TEMP_SS__8_ROGERS1A_8_138_Line | Sandow-Austrop 345-kV double circuit | 1.4
23 | TEMP_PEC__8_TEMP_SS__8_138_Line | Sandow-Austrop 345-kV double circuit | 3.5
23 | SANDOW1_8_ELGIN_SS__8_138_Line | Sandow-Austrop 345-kV double circuit | 7.9
23 | SANDOW1_8_SALTY_P_8_138_Line | Sandow-Austrop 345-kV double circuit | 8
23 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV double circuit | 0
23 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Sandow-Austrop 345-kV double circuit | 3.1
23 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Sandow-Austrop 345-kV double circuit | 0
23 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Sandow-Austrop 345-kV double circuit | 0
23 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Sandow-Austrop 345-kV double circuit | 3.3
23 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Sandow-Austrop 345-kV double circuit | 3.3
23 | ROGERS1A_8_SANDOW1_8_138_Line | Sandow-Austrop 345-kV double circuit | 1.4
23 | THOUSE__5_LAKE_CRK2_5_345_Line | Sandow-Austrop 345-kV double circuit | 7.1
24 | CSC_3 | Austrop-Garfield 345-kV double circuit | 32.6
24 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Austrop-Garfield 345-kV double circuit | 3.2
24 | THOUSE__5_LAKE_CRK1_5_345_Line | Austrop-Garfield 345-kV double circuit | 6.6
24 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Austrop-Garfield 345-kV double circuit | 18.5
24 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Austrop-Garfield 345-kV double circuit | 2.5
24 | THOUSE__5_TEMP_PEC__5_345_Line | Austrop-Garfield 345-kV double circuit | 16.6
24 | TEMP_PEC__5_TEMP_SS__5_345_Line | Austrop-Garfield 345-kV double circuit | 15.6
24 | TEMP_SS__8_ROGERS1A_8_138_Line | Austrop-Garfield 345-kV double circuit | 2.2
24 | TEMP_PEC__8_TEMP_SS__8_138_Line | Austrop-Garfield 345-kV double circuit | 2.9
24 | SANDOW1_8_ELGIN_SS__8_138_Line | Austrop-Garfield 345-kV double circuit | 3.1
24 | SANDOW1_8_SALTY_P_8_138_Line | Austrop-Garfield 345-kV double circuit | 3.2
24 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Austrop-Garfield 345-kV double circuit | 15.5
24 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Austrop-Garfield 345-kV double circuit | 0
24 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Austrop-Garfield 345-kV double circuit | 0
24 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Austrop-Garfield 345-kV double circuit | 15.4
24 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Austrop-Garfield 345-kV double circuit | 2.8
24 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Austrop-Garfield 345-kV double circuit | 2.8
24 | ROGERS1A_8_SANDOW1_8_138_Line | Austrop-Garfield 345-kV double circuit | 2.2
24 | THOUSE__5_LAKE_CRK2_5_345_Line | Austrop-Garfield 345-kV double circuit | 7.8
25 | CSC_3 | Garfield-Lytton 345-kV double circuit | 33.5
25 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Garfield-Lytton 345-kV double circuit | 3.1
25 | THOUSE__5_LAKE_CRK1_5_345_Line | Garfield-Lytton 345-kV double circuit | 6.6
25 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Garfield-Lytton 345-kV double circuit | 18.8
25 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Garfield-Lytton 345-kV double circuit | 2.5
25 | THOUSE__5_TEMP_PEC__5_345_Line | Garfield-Lytton 345-kV double circuit | 16.8
25 | TEMP_PEC__5_TEMP_SS__5_345_Line | Garfield-Lytton 345-kV double circuit | 16
25 | TEMP_SS__8_ROGERS1A_8_138_Line | Garfield-Lytton 345-kV double circuit | 2.2
25 | TEMP_PEC__8_TEMP_SS__8_138_Line | Garfield-Lytton 345-kV double circuit | 2.8
25 | SANDOW1_8_ELGIN_SS__8_138_Line | Garfield-Lytton 345-kV double circuit | 2.8
25 | SANDOW1_8_SALTY_P_8_138_Line | Garfield-Lytton 345-kV double circuit | 2.9
25 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Garfield-Lytton 345-kV double circuit | 16.3
25 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Garfield-Lytton 345-kV double circuit | 0
25 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Garfield-Lytton 345-kV double circuit | 7.3
25 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Garfield-Lytton 345-kV double circuit | 16.2
25 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Garfield-Lytton 345-kV double circuit | 2.7
25 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Garfield-Lytton 345-kV double circuit | 2.7
25 | ROGERS1A_8_SANDOW1_8_138_Line | Garfield-Lytton 345-kV double circuit | 2.2
25 | THOUSE__5_LAKE_CRK2_5_345_Line | Garfield-Lytton 345-kV double circuit | 7.8
26 | CSC_3 | Lytton-Zorn 345-kV double circuit | 32.6
26 | BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Lytton-Zorn 345-kV double circuit | 3.2
26 | THOUSE__5_LAKE_CRK1_5_345_Line | Lytton-Zorn 345-kV double circuit | 6.6
26 | LAKE_CRK1_5_TEMP_SS__5_345_Line | Lytton-Zorn 345-kV double circuit | 18.3
26 | LAKE_CRK1_8_TEMP_PEC__8_138_Line | Lytton-Zorn 345-kV double circuit | 2.4
26 | THOUSE__5_TEMP_PEC__5_345_Line | Lytton-Zorn 345-kV double circuit | 16.4
26 | TEMP_PEC__5_TEMP_SS__5_345_Line | Lytton-Zorn 345-kV double circuit | 15.6
26 | TEMP_SS__8_ROGERS1A_8_138_Line | Lytton-Zorn 345-kV double circuit | 2.1
26 | TEMP_PEC__8_TEMP_SS__8_138_Line | Lytton-Zorn 345-kV double circuit | 2.7
26 | SANDOW1_8_ELGIN_SS__8_138_Line | Lytton-Zorn 345-kV double circuit | 2.8
26 | SANDOW1_8_SALTY_P_8_138_Line | Lytton-Zorn 345-kV double circuit | 2.8
26 | SANDOW__5_L_AUSTRO5_1Y_345_Line | Lytton-Zorn 345-kV double circuit | 15.8
26 | L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Lytton-Zorn 345-kV double circuit | 0
26 | L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Lytton-Zorn 345-kV double circuit | 11.7
26 | SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Lytton-Zorn 345-kV double circuit | 15.7
26 | L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Lytton-Zorn 345-kV double circuit | 2.7
26 | L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Lytton-Zorn 345-kV double circuit | 2.7
26 | ROGERS1A_8_SANDOW1_8_138_Line | Lytton-Zorn 345-kV double circuit | 2.1
26 | THOUSE__5_LAKE_CRK2_5_345_Line | Lytton-Zorn 345-kV double circuit | 7.7

## W-N PTDFs
Contingency # | Element | Contingency | PTDF | Top 3 plants with the highest impact in each direction
Base Case | CSC_1 | Base Case | 34.9
Base Case | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Base Case | 13.9 | Roscoe Wind | 28.678 | Panther Creek Wind | 18.4765 | Falcon Seaboard | 18.3784 | Graham | -3.8567 | Wise County | -2.1856 | Wichita Falls | -1.5456
Base Case | MURRY_P8_GRAHAMSES1_8_138_Line | Base Case | 3.5 | Whirlwind | 12.1545 | Red Canyon | 6.135 | Kinder Morgan | 5.1417 | Graham | -6.8374 | Barton Wind | -3.8747 | Morris Sheperd | -2.0954
Base Case | SWEETWTR_5_GRAHAMSES1_5_345_Line | Base Case | 13.9 | Sweetwater Gas | 39.0907 | Panther Creek Wind | 20.7435 | Falcon Seaboard | 20.6393 | Graham | -4.099 | Wise County | -2.3229 | Wichita Falls | -1.6427
Base Case | WILLOWCK_5_JACKSBRO_5_345_Line | Base Case | -14.9 | Wichita Falls | -19.5722 | Oklaunion | -18.4202 | Graham | -16.0424 | Wise County | 38.3821 | Comanche Peak | 2.559 | Wolf Hollow | 2.4597
Base Case | WILLOWCK_5_PARKER_5_345_Line | Base Case | 12.1 | Wise County | 61.6179 | Wichita Falls | 19.5722 | Oklaunion | 18.4202 | Comanche Peak | -2.559 | Wolf Hollow | -2.4597 | Decordova | -2.2583
Base Case | FISHRDSS1_5_BOWMAN_5_345_Line | Base Case | 9.2 | Oklaunion | 51.6566 | Whirlwind | 16.7798 | Calahan Divide | 10.2899 | Wise County | -3.1904 | Graham | -1.9424 | Spencer | -1.2573
Base Case | BOWMAN_5_JACKSBRO_5_345_Line | Base Case | 9.6 | Wichita Falls | 30.8549 | Oklaunion | 25.7533 | Whirlwind | 12.887 | Wise County | -8.0773 | Spencer | -2.1946 | North Lake | -1.4103
Base Case | OKLA7A_FISHRDSS1_5_345_Line | Base Case | 10.7 | Oklaunion | 59.4576 | Whirlwind | 18.3929 | Horse Hollow | 12.0608 | Wichita Falls | -9.897 | Wise County | -2.3343 | Jack County | -2.1611
Base Case | JACKSBRO_5_W_DENT_5_345_Line | Base Case | 11.5 | Wichita Falls | 14.4494 | Oklaunion | 14.0812 | Graham | 13.2818 | Spencer | -8.6676 | Denison Dam | -3.0429 | Valley | -2.9135
Base Case | GRAHAMSES1_5_JACKSBRO_5_345_Line | Base Case | 16.9 | Graham | 23.9023 | Sweetwater Gas | 18.3703 | Mesquite Wind | 17.6457 | Wise County | -17.1434 | Spencer | -4.9114 | Denison Dam | -2.4359
Base Case | GRAHAMSES1_5_BENBRK_5_345_Line | Base Case | 16.3 | Graham | 21.1966 | Mesquite Wind | 17.5585 | Sweetwater Gas | 17.4898 | Decordova | -3.2744 | Handley | -2.4734 | Midlothian | -2.1049
Base Case | GRAHAMSES1_8_GRAHAME_8_138_Line | Base Case | 2.4 | Graham | 13.1012 | Whirlwind | 3.9555 | Wichita Falls | 3.5844 | Barton Wind | -45.3353 | Morris Sheperd | -12.7238 | Miller | -11.6708
Base Case | LONGCREK_5_GRAHAMSES1_5_345_Line | Base Case | 23.9 | Mesquite Wind | 48.87 | Horse Hollow | 26.4627 | Buffalo Gap | 26.4627 | Graham | -7.1932 | Wise County | -3.555 | Spencer | -2.2291
Base Case | ABMULCE7_LONGCREK_5_345_Line | Base Case | 13.1 | Buffalo Gap | 26.4627 | Horse Hollow | 26.4627 | Calahan Divide | 24.5186 | Mesquite Wind | -51.13 | Graham | -7.1932 | Wise County | -3.555
Base Case | PARKER_5_BENBRK_A_T5_345_Line | Base Case | 8.1 | Wise County | 22.7581 | Wichita Falls | 11.7122 | Oklaunion | 11.1005 | Decordova | -7.6514 | Handley | -4.4771 | Midlothian | -3.2371
Base Case | COMCHESS1_5_COMCHPKW_5_345_Line | Base Case | 16.7 | Capricorn Ridge | 18.6028 | Goat Mountain | 17.8564 | Horse Hollow | 17.4131 | Comanche Peak | -7.9485 | Wolf Hollow | -7.3327 | Decordova | -5.2395
Base Case | SARC7A_COMCHESS1_5_345_Line | Base Case | 17.1 | Capricorn Ridge | 20.8431 | Goat Mountain | 20.0035 | Buffalo Gap | 18.569 | Comanche Peak | -4.1512 | Wolf Hollow | -3.8027 | Decordova | -2.698
Base Case | LKAROWHD_8_NEWPRT_P8_138_Line | Base Case | 2.5 | Wichita Falls | 7.118 | Oklaunion | 3.7176 | Graham | 2.9342 | Jack County | -10.2314 | North Texas | -3.1864 | Miller | -1.1498
Base Case | GRAHAMSW_8_BARTON_8_138_Line | Base Case | 2.5 | Graham | 11.8852 | Wichita Falls | 4.319 | Whirlwind | 4.1392 | Barton Wind | -48.8002 | Morris Sheperd | -13.6433 | Miller | -12.4529
Base Case | GRAHAME_8_GRAHAMSW_8_138_Line | Base Case | 2.4 | Graham | 13.0762 | Whirlwind | 3.9306 | Wichita Falls | 3.5595 | Barton Wind | -45.3602 | Morris Sheperd | -12.7487 | Miller | -11.6957
Base Case | BARTON_8_ORAN1_8_138_Line | Base Case | 4.6 | Barton Wind | 51.1998 | Graham | 11.8852 | Wichita Falls | 4.319 | Morris Sheperd | -13.6433 | Miller | -12.4529 | North Texas | -11.6206
Base Case | LEONSW_8_FLATCRK_T8_138_Line | Base Case | 3.3 | Graham | 6.4151 | Whirlwind | 3.6461 | Trent Mesa Wind | 3.2338 | Clipper Silver Star | -30.5709 | Miller | -3.7764 | Whitney | -1.6713
Base Case | LINGLVLL_P8_STPHNVIL_8_138_Line | Base Case | 3.3 | Clipper Silver Star | 69.4219 | Graham | 6.4079 | Trent Mesa Wind | 3.2266 | Miller | -3.7836 | Whitney | -1.6785 | Bosque | -1.6195
Base Case | FLATCRK_T8_LINGLVLL_P8_138_Line | Base Case | 3.3 | Clipper Silver Star | 69.4291 | Graham | 6.4151 | Whirlwind | 3.6461 | Miller | -3.7764 | Whitney | -1.6713 | Bosque | -1.6123
Base Case | PAIP4B_MURRY_P8_138_Line | Base Case | 3.5 | Whirlwind | 12.1582 | Red Canyon | 6.1387 | Green Mountain | 5.1454 | Graham | -6.8337 | Barton Wind | -3.871 | Morris Sheperd | -2.0917
Base Case | BLF_CRK7A_ABMULCE7_345_Line | Base Case | 9 | Buffalo Gap | 46.8679 | Horse Hollow | 46.8679 | Capricorn Ridge | 10.1611 | Mesquite Wind | -17.3137 | Sweetwater Wind | -11.4264 | Oklaunion | -11.1421
1 | CSC_1 | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 0
1 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 12.3 | Roscoe Wind | 27.5103 | Panther Creek Wind | 17.4128 | Falcon Seaboard | 17.3252 | Graham | -5.6229 | Wichita Falls | -2.7669 | Wise County | -2.4256
1 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 3.4 | Whirlwind | 12.0844 | Red Canyon | 6.0632 | Kinder Morgan | 5.0698 | Graham | -6.9101 | Barton Wind | -3.9166 | Morris Sheperd | -2.1318
1 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 12.2 | Sweetwater Gas | 36.1591 | Panther Creek Wind | 17.9413 | Falcon Seaboard | 17.8411 | Graham | -6.3183 | Wichita Falls | -3.2328 | Wise County | -2.7882
1 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | -30.9 | Graham | -36.6854 | Wichita Falls | -34.3161 | Oklaunion | -33.7918 | Wise County | 34.3009 | Decordova | 4.4903 | Comanche Peak | 4.2049
1 | WILLOWCK_5_PARKER_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 28 | Wise County | 65.6991 | Graham | 36.6854 | Wichita Falls | 34.3161 | Decordova | -4.4903 | Comanche Peak | -4.2049 | Wolf Hollow | -4.167
1 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 8.9 | Oklaunion | 51.3356 | Whirlwind | 16.4648 | Calahan Divide | 9.996 | Wise County | -3.2933 | Graham | -2.3699 | Spencer | -1.2643
1 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 14.8 | Wichita Falls | 35.6586 | Oklaunion | 30.761 | Whirlwind | 17.8222 | Wise County | -6.7383 | Spencer | -2.2015 | North Lake | -1.8228
1 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 10.7 | Oklaunion | 59.5422 | Whirlwind | 18.4771 | Horse Hollow | 12.1403 | Wichita Falls | -9.8164 | Wise County | -2.3219 | Jack County | -2.1489
1 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 19.3 | Graham | 23.319 | Wichita Falls | 21.6375 | Oklaunion | 21.5699 | Spencer | -8.6415 | Denison Dam | -3.5237 | Valley | -3.4263
1 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 35.4 | Graham | 47.8593 | Sweetwater Gas | 38.0698 | Mesquite Wind | 37.3908 | Wise County | -12.3157 | Spencer | -4.9122 | North Lake | -3.7016
1 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 0
1 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.3 | Graham | 14.9742 | Whirlwind | 5.7618 | Wichita Falls | 5.3458 | Barton Wind | -44.2564 | Morris Sheperd | -11.7866 | Miller | -11.317
1 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 20.6 | Mesquite Wind | 45.3407 | Horse Hollow | 23.5056 | Buffalo Gap | 23.5056 | Graham | -11.4741 | Wise County | -4.4506 | Wichita Falls | -3.9373
1 | ABMULCE7_LONGCREK_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 9.8 | Buffalo Gap | 23.5056 | Horse Hollow | 23.5056 | Calahan Divide | 21.5808 | Mesquite Wind | -54.6593 | Graham | -11.4741 | Wise County | -4.4506
1 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 13 | Wise County | 25.8148 | Graham | 17.3672 | Wichita Falls | 16.658 | Decordova | -8.9297 | Handley | -5.3675 | Midlothian | -3.9772
1 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 21.4 | Capricorn Ridge | 22.7591 | Goat Mountain | 22.0897 | Buffalo Gap | 21.5841 | Comanche Peak | -8.4267 | Wolf Hollow | -7.832 | Decordova | -5.9168
1 | SARC7A_COMCHESS1_5_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 21.3 | Capricorn Ridge | 24.6072 | Goat Mountain | 23.8374 | Buffalo Gap | 22.3464 | Comanche Peak | -4.5841 | Wolf Hollow | -4.2549 | Decordova | -3.3123
1 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 3.8 | Wichita Falls | 8.2657 | Oklaunion | 4.9131 | Graham | 4.1546 | Jack County | -10.0209 | North Texas | -2.9804 | Spencer | -0.968
1 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.4 | Graham | 13.7696 | Wichita Falls | 6.0911 | Whirlwind | 5.9565 | Barton Wind | -47.7148 | Morris Sheperd | -12.7004 | Miller | -12.097
1 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.3 | Graham | 14.9493 | Whirlwind | 5.7369 | Wichita Falls | 5.3208 | Barton Wind | -44.2814 | Morris Sheperd | -11.8116 | Miller | -11.3419
1 | BARTON_8_ORAN1_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 6.5 | Barton Wind | 52.2852 | Graham | 13.7696 | Wichita Falls | 6.0911 | Morris Sheperd | -12.7004 | Miller | -12.097 | North Texas | -11.3026
1 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.6 | Graham | 7.6173 | Whirlwind | 4.8253 | Trent Mesa Wind | 4.4145 | Clipper Silver Star | -30.1457 | Miller | -3.5435 | Whitney | -1.7175
1 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.6 | Clipper Silver Star | 69.8471 | Graham | 7.6101 | Whirlwind | 4.8181 | Miller | -3.5507 | Whitney | -1.7247 | Bosque | -1.6745
1 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 4.6 | Clipper Silver Star | 69.8543 | Graham | 7.6173 | Whirlwind | 4.8253 | Miller | -3.5435 | Whitney | -1.7175 | Bosque | -1.6674
1 | PAIP4B_MURRY_P8_138_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 3.4 | Whirlwind | 12.3238 | Red Canyon | 6.3193 | Trent Mesa Wind | 5.3661 | Graham | -6.9165 | Barton Wind | -3.9331 | Morris Sheperd | -2.1274
1 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 6.4 | Buffalo Gap | 45.1512 | Horse Hollow | 45.1512 | Capricorn Ridge | 8.4023 | Mesquite Wind | -19.6094 | Sweetwater Wind | -13.4551 | Oklaunion | -13.2641
2 | CSC_1 | Tonkawa-Graham 345-kV line | 33
2 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Tonkawa-Graham 345-kV line | 0
2 | MURRY_P8_GRAHAMSES1_8_138_Line | Tonkawa-Graham 345-kV line | 4
2 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Tonkawa-Graham 345-kV line | 18.2
2 | WILLOWCK_5_JACKSBRO_5_345_Line | Tonkawa-Graham 345-kV line | -14.5
2 | WILLOWCK_5_PARKER_5_345_Line | Tonkawa-Graham 345-kV line | 11.6
2 | FISHRDSS1_5_BOWMAN_5_345_Line | Tonkawa-Graham 345-kV line | 10.8
2 | BOWMAN_5_JACKSBRO_5_345_Line | Tonkawa-Graham 345-kV line | 10
2 | OKLA7A_FISHRDSS1_5_345_Line | Tonkawa-Graham 345-kV line | 12.3
2 | JACKSBRO_5_W_DENT_5_345_Line | Tonkawa-Graham 345-kV line | 11.1
2 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Tonkawa-Graham 345-kV line | 15.6
2 | GRAHAMSES1_5_BENBRK_5_345_Line | Tonkawa-Graham 345-kV line | 15.4
2 | GRAHAMSES1_8_GRAHAME_8_138_Line | Tonkawa-Graham 345-kV line | 2.3
2 | LONGCREK_5_GRAHAMSES1_5_345_Line | Tonkawa-Graham 345-kV line | 28.1
2 | ABMULCE7_LONGCREK_5_345_Line | Tonkawa-Graham 345-kV line | 17.3
2 | PARKER_5_BENBRK_A_T5_345_Line | Tonkawa-Graham 345-kV line | 7.7
2 | COMCHESS1_5_COMCHPKW_5_345_Line | Tonkawa-Graham 345-kV line | 18.5
2 | SARC7A_COMCHESS1_5_345_Line | Tonkawa-Graham 345-kV line | 18.9
2 | LKAROWHD_8_NEWPRT_P8_138_Line | Tonkawa-Graham 345-kV line | 2.5
2 | GRAHAMSW_8_BARTON_8_138_Line | Tonkawa-Graham 345-kV line | 2.5
2 | GRAHAME_8_GRAHAMSW_8_138_Line | Tonkawa-Graham 345-kV line | 2.3
2 | BARTON_8_ORAN1_8_138_Line | Tonkawa-Graham 345-kV line | 4.5
2 | LEONSW_8_FLATCRK_T8_138_Line | Tonkawa-Graham 345-kV line | 3.5
2 | LINGLVLL_P8_STPHNVIL_8_138_Line | Tonkawa-Graham 345-kV line | 3.4
2 | FLATCRK_T8_LINGLVLL_P8_138_Line | Tonkawa-Graham 345-kV line | 3.4
2 | PAIP4B_MURRY_P8_138_Line | Tonkawa-Graham 345-kV line | 4
2 | BLF_CRK7A_ABMULCE7_345_Line | Tonkawa-Graham 345-kV line | 9.8
3 | CSC_1 | Murray-Graham 138-kV line | 34.8
3 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Murray-Graham 138-kV line | 14.3
3 | MURRY_P8_GRAHAMSES1_8_138_Line | Murray-Graham 138-kV line | 0
3 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Murray-Graham 138-kV line | 14.4
3 | WILLOWCK_5_JACKSBRO_5_345_Line | Murray-Graham 138-kV line | -14.9
3 | WILLOWCK_5_PARKER_5_345_Line | Murray-Graham 138-kV line | 12.1
3 | FISHRDSS1_5_BOWMAN_5_345_Line | Murray-Graham 138-kV line | 9.7
3 | BOWMAN_5_JACKSBRO_5_345_Line | Murray-Graham 138-kV line | 9.6
3 | OKLA7A_FISHRDSS1_5_345_Line | Murray-Graham 138-kV line | 11.4
3 | JACKSBRO_5_W_DENT_5_345_Line | Murray-Graham 138-kV line | 11.5
3 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Murray-Graham 138-kV line | 16.8
3 | GRAHAMSES1_5_BENBRK_5_345_Line | Murray-Graham 138-kV line | 16.3
3 | GRAHAMSES1_8_GRAHAME_8_138_Line | Murray-Graham 138-kV line | 2
3 | LONGCREK_5_GRAHAMSES1_5_345_Line | Murray-Graham 138-kV line | 24.8
3 | ABMULCE7_LONGCREK_5_345_Line | Murray-Graham 138-kV line | 14
3 | PARKER_5_BENBRK_A_T5_345_Line | Murray-Graham 138-kV line | 8
3 | COMCHESS1_5_COMCHPKW_5_345_Line | Murray-Graham 138-kV line | 17
3 | SARC7A_COMCHESS1_5_345_Line | Murray-Graham 138-kV line | 17.4
3 | LKAROWHD_8_NEWPRT_P8_138_Line | Murray-Graham 138-kV line | 2.5
3 | GRAHAMSW_8_BARTON_8_138_Line | Murray-Graham 138-kV line | 2.2
3 | GRAHAME_8_GRAHAMSW_8_138_Line | Murray-Graham 138-kV line | 2
3 | BARTON_8_ORAN1_8_138_Line | Murray-Graham 138-kV line | 4.2
3 | LEONSW_8_FLATCRK_T8_138_Line | Murray-Graham 138-kV line | 3.3
3 | LINGLVLL_P8_STPHNVIL_8_138_Line | Murray-Graham 138-kV line | 3.2
3 | FLATCRK_T8_LINGLVLL_P8_138_Line | Murray-Graham 138-kV line | 3.2
3 | PAIP4B_MURRY_P8_138_Line | Murray-Graham 138-kV line | 0
3 | BLF_CRK7A_ABMULCE7_345_Line | Murray-Graham 138-kV line | 9.1
4 | CSC_1 | Sweetwater-Graham 345-kV line | 33
4 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Sweetwater-Graham 345-kV line | 18
4 | MURRY_P8_GRAHAMSES1_8_138_Line | Sweetwater-Graham 345-kV line | 4
4 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Sweetwater-Graham 345-kV line | 0
4 | WILLOWCK_5_JACKSBRO_5_345_Line | Sweetwater-Graham 345-kV line | -14.4
4 | WILLOWCK_5_PARKER_5_345_Line | Sweetwater-Graham 345-kV line | 11.6
4 | FISHRDSS1_5_BOWMAN_5_345_Line | Sweetwater-Graham 345-kV line | 10.8
4 | BOWMAN_5_JACKSBRO_5_345_Line | Sweetwater-Graham 345-kV line | 10
4 | OKLA7A_FISHRDSS1_5_345_Line | Sweetwater-Graham 345-kV line | 12.4
4 | JACKSBRO_5_W_DENT_5_345_Line | Sweetwater-Graham 345-kV line | 11.1
4 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Sweetwater-Graham 345-kV line | 15.5
4 | GRAHAMSES1_5_BENBRK_5_345_Line | Sweetwater-Graham 345-kV line | 15.4
4 | GRAHAMSES1_8_GRAHAME_8_138_Line | Sweetwater-Graham 345-kV line | 2.3
4 | LONGCREK_5_GRAHAMSES1_5_345_Line | Sweetwater-Graham 345-kV line | 28.3
4 | ABMULCE7_LONGCREK_5_345_Line | Sweetwater-Graham 345-kV line | 17.4
4 | PARKER_5_BENBRK_A_T5_345_Line | Sweetwater-Graham 345-kV line | 7.7
4 | COMCHESS1_5_COMCHPKW_5_345_Line | Sweetwater-Graham 345-kV line | 18.6
4 | SARC7A_COMCHESS1_5_345_Line | Sweetwater-Graham 345-kV line | 18.9
4 | LKAROWHD_8_NEWPRT_P8_138_Line | Sweetwater-Graham 345-kV line | 2.5
4 | GRAHAMSW_8_BARTON_8_138_Line | Sweetwater-Graham 345-kV line | 2.5
4 | GRAHAME_8_GRAHAMSW_8_138_Line | Sweetwater-Graham 345-kV line | 2.3
4 | BARTON_8_ORAN1_8_138_Line | Sweetwater-Graham 345-kV line | 4.5
4 | LEONSW_8_FLATCRK_T8_138_Line | Sweetwater-Graham 345-kV line | 3.5
4 | LINGLVLL_P8_STPHNVIL_8_138_Line | Sweetwater-Graham 345-kV line | 3.4
4 | FLATCRK_T8_LINGLVLL_P8_138_Line | Sweetwater-Graham 345-kV line | 3.4
4 | PAIP4B_MURRY_P8_138_Line | Sweetwater-Graham 345-kV line | 4
4 | BLF_CRK7A_ABMULCE7_345_Line | Sweetwater-Graham 345-kV line | 9.8
5 | CSC_1 | Willow Creek-Jacksboro 345-kV line | 42.5
5 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Willow Creek-Jacksboro 345-kV line | 13.7
5 | MURRY_P8_GRAHAMSES1_8_138_Line | Willow Creek-Jacksboro 345-kV line | 3.5
5 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Willow Creek-Jacksboro 345-kV line | 13.7
5 | WILLOWCK_5_JACKSBRO_5_345_Line | Willow Creek-Jacksboro 345-kV line | 0
5 | WILLOWCK_5_PARKER_5_345_Line | Willow Creek-Jacksboro 345-kV line | -2.9
5 | FISHRDSS1_5_BOWMAN_5_345_Line | Willow Creek-Jacksboro 345-kV line | 8.5
5 | BOWMAN_5_JACKSBRO_5_345_Line | Willow Creek-Jacksboro 345-kV line | 6.7
5 | OKLA7A_FISHRDSS1_5_345_Line | Willow Creek-Jacksboro 345-kV line | 10.1
5 | JACKSBRO_5_W_DENT_5_345_Line | Willow Creek-Jacksboro 345-kV line | 16.5
5 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Willow Creek-Jacksboro 345-kV line | 9.8
5 | GRAHAMSES1_5_BENBRK_5_345_Line | Willow Creek-Jacksboro 345-kV line | 19.1
5 | GRAHAMSES1_8_GRAHAME_8_138_Line | Willow Creek-Jacksboro 345-kV line | 2.8
5 | LONGCREK_5_GRAHAMSES1_5_345_Line | Willow Creek-Jacksboro 345-kV line | 23.6
5 | ABMULCE7_LONGCREK_5_345_Line | Willow Creek-Jacksboro 345-kV line | 12.8
5 | PARKER_5_BENBRK_A_T5_345_Line | Willow Creek-Jacksboro 345-kV line | 4.6
5 | COMCHESS1_5_COMCHPKW_5_345_Line | Willow Creek-Jacksboro 345-kV line | 17.7
5 | SARC7A_COMCHESS1_5_345_Line | Willow Creek-Jacksboro 345-kV line | 17.9
5 | LKAROWHD_8_NEWPRT_P8_138_Line | Willow Creek-Jacksboro 345-kV line | 2.9
5 | GRAHAMSW_8_BARTON_8_138_Line | Willow Creek-Jacksboro 345-kV line | 2.9
5 | GRAHAME_8_GRAHAMSW_8_138_Line | Willow Creek-Jacksboro 345-kV line | 2.8
5 | BARTON_8_ORAN1_8_138_Line | Willow Creek-Jacksboro 345-kV line | 5
5 | LEONSW_8_FLATCRK_T8_138_Line | Willow Creek-Jacksboro 345-kV line | 3.6
5 | LINGLVLL_P8_STPHNVIL_8_138_Line | Willow Creek-Jacksboro 345-kV line | 3.6
5 | FLATCRK_T8_LINGLVLL_P8_138_Line | Willow Creek-Jacksboro 345-kV line | 3.6
5 | PAIP4B_MURRY_P8_138_Line | Willow Creek-Jacksboro 345-kV line | 3.5
5 | BLF_CRK7A_ABMULCE7_345_Line | Willow Creek-Jacksboro 345-kV line | 8.4
6 | CSC_1 | Willow Creek-Parker 345-kV line | 41
6 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Willow Creek-Parker 345-kV line | 13.7
6 | MURRY_P8_GRAHAMSES1_8_138_Line | Willow Creek-Parker 345-kV line | 3.5
6 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Willow Creek-Parker 345-kV line | 13.8
6 | WILLOWCK_5_JACKSBRO_5_345_Line | Willow Creek-Parker 345-kV line | -2.9
6 | WILLOWCK_5_PARKER_5_345_Line | Willow Creek-Parker 345-kV line | 0
6 | FISHRDSS1_5_BOWMAN_5_345_Line | Willow Creek-Parker 345-kV line | 8.6
6 | BOWMAN_5_JACKSBRO_5_345_Line | Willow Creek-Parker 345-kV line | 7.3
6 | OKLA7A_FISHRDSS1_5_345_Line | Willow Creek-Parker 345-kV line | 10.2
6 | JACKSBRO_5_W_DENT_5_345_Line | Willow Creek-Parker 345-kV line | 15.6
6 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Willow Creek-Parker 345-kV line | 11.1
6 | GRAHAMSES1_5_BENBRK_5_345_Line | Willow Creek-Parker 345-kV line | 18.6
6 | GRAHAMSES1_8_GRAHAME_8_138_Line | Willow Creek-Parker 345-kV line | 2.7
6 | LONGCREK_5_GRAHAMSES1_5_345_Line | Willow Creek-Parker 345-kV line | 23.7
6 | ABMULCE7_LONGCREK_5_345_Line | Willow Creek-Parker 345-kV line | 12.8
6 | PARKER_5_BENBRK_A_T5_345_Line | Willow Creek-Parker 345-kV line | 5.3
6 | COMCHESS1_5_COMCHPKW_5_345_Line | Willow Creek-Parker 345-kV line | 17.5
6 | SARC7A_COMCHESS1_5_345_Line | Willow Creek-Parker 345-kV line | 17.7
6 | LKAROWHD_8_NEWPRT_P8_138_Line | Willow Creek-Parker 345-kV line | 2.8
6 | GRAHAMSW_8_BARTON_8_138_Line | Willow Creek-Parker 345-kV line | 2.8
6 | GRAHAME_8_GRAHAMSW_8_138_Line | Willow Creek-Parker 345-kV line | 2.7
6 | BARTON_8_ORAN1_8_138_Line | Willow Creek-Parker 345-kV line | 4.9
6 | LEONSW_8_FLATCRK_T8_138_Line | Willow Creek-Parker 345-kV line | 3.5
6 | LINGLVLL_P8_STPHNVIL_8_138_Line | Willow Creek-Parker 345-kV line | 3.5
6 | FLATCRK_T8_LINGLVLL_P8_138_Line | Willow Creek-Parker 345-kV line | 3.5
6 | PAIP4B_MURRY_P8_138_Line | Willow Creek-Parker 345-kV line | 3.5
6 | BLF_CRK7A_ABMULCE7_345_Line | Willow Creek-Parker 345-kV line | 8.6
7 | CSC_1 | Bowman-Jacksboro 345-kV line | 36.8
7 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Bowman-Jacksboro 345-kV line | 14
7 | MURRY_P8_GRAHAMSES1_8_138_Line | Bowman-Jacksboro 345-kV line | 3.5
7 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Bowman-Jacksboro 345-kV line | 14.1
7 | WILLOWCK_5_JACKSBRO_5_345_Line | Bowman-Jacksboro 345-kV line | -12.7
7 | WILLOWCK_5_PARKER_5_345_Line | Bowman-Jacksboro 345-kV line | 9.8
7 | FISHRDSS1_5_BOWMAN_5_345_Line | Bowman-Jacksboro 345-kV line | 7.4
7 | BOWMAN_5_JACKSBRO_5_345_Line | Bowman-Jacksboro 345-kV line | 0
7 | OKLA7A_FISHRDSS1_5_345_Line | Bowman-Jacksboro 345-kV line | 9.2
7 | JACKSBRO_5_W_DENT_5_345_Line | Bowman-Jacksboro 345-kV line | 10.2
7 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Bowman-Jacksboro 345-kV line | 22.9
7 | GRAHAMSES1_5_BENBRK_5_345_Line | Bowman-Jacksboro 345-kV line | 17.1
7 | GRAHAMSES1_8_GRAHAME_8_138_Line | Bowman-Jacksboro 345-kV line | 2.6
7 | LONGCREK_5_GRAHAMSES1_5_345_Line | Bowman-Jacksboro 345-kV line | 24.5
7 | ABMULCE7_LONGCREK_5_345_Line | Bowman-Jacksboro 345-kV line | 13.6
7 | PARKER_5_BENBRK_A_T5_345_Line | Bowman-Jacksboro 345-kV line | 7.3
7 | COMCHESS1_5_COMCHPKW_5_345_Line | Bowman-Jacksboro 345-kV line | 17.2
7 | SARC7A_COMCHESS1_5_345_Line | Bowman-Jacksboro 345-kV line | 17.5
7 | LKAROWHD_8_NEWPRT_P8_138_Line | Bowman-Jacksboro 345-kV line | 3
7 | GRAHAMSW_8_BARTON_8_138_Line | Bowman-Jacksboro 345-kV line | 2.8
7 | GRAHAME_8_GRAHAMSW_8_138_Line | Bowman-Jacksboro 345-kV line | 2.6
7 | BARTON_8_ORAN1_8_138_Line | Bowman-Jacksboro 345-kV line | 4.8
7 | LEONSW_8_FLATCRK_T8_138_Line | Bowman-Jacksboro 345-kV line | 3.5
7 | LINGLVLL_P8_STPHNVIL_8_138_Line | Bowman-Jacksboro 345-kV line | 3.5
7 | FLATCRK_T8_LINGLVLL_P8_138_Line | Bowman-Jacksboro 345-kV line | 3.5
7 | PAIP4B_MURRY_P8_138_Line | Bowman-Jacksboro 345-kV line | 3.5
7 | BLF_CRK7A_ABMULCE7_345_Line | Bowman-Jacksboro 345-kV line | 8.6
8 | CSC_1 | Oklaunion-Fisher Road 345-kV line | 35
8 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road 345-kV line | 15.2
8 | MURRY_P8_GRAHAMSES1_8_138_Line | Oklaunion-Fisher Road 345-kV line | 4.3
8 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road 345-kV line | 15.4
8 | WILLOWCK_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road 345-kV line | -13.9
8 | WILLOWCK_5_PARKER_5_345_Line | Oklaunion-Fisher Road 345-kV line | 11
8 | FISHRDSS1_5_BOWMAN_5_345_Line | Oklaunion-Fisher Road 345-kV line | -0.1
8 | BOWMAN_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road 345-kV line | 5.9
8 | OKLA7A_FISHRDSS1_5_345_Line | Oklaunion-Fisher Road 345-kV line | 0
8 | JACKSBRO_5_W_DENT_5_345_Line | Oklaunion-Fisher Road 345-kV line | 10.9
8 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road 345-kV line | 18.8
8 | GRAHAMSES1_5_BENBRK_5_345_Line | Oklaunion-Fisher Road 345-kV line | 16.3
8 | GRAHAMSES1_8_GRAHAME_8_138_Line | Oklaunion-Fisher Road 345-kV line | 2.4
8 | LONGCREK_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road 345-kV line | 28.4
8 | ABMULCE7_LONGCREK_5_345_Line | Oklaunion-Fisher Road 345-kV line | 17.6
8 | PARKER_5_BENBRK_A_T5_345_Line | Oklaunion-Fisher Road 345-kV line | 7.6
8 | COMCHESS1_5_COMCHPKW_5_345_Line | Oklaunion-Fisher Road 345-kV line | 18
8 | SARC7A_COMCHESS1_5_345_Line | Oklaunion-Fisher Road 345-kV line | 18.3
8 | LKAROWHD_8_NEWPRT_P8_138_Line | Oklaunion-Fisher Road 345-kV line | 2.2
8 | GRAHAMSW_8_BARTON_8_138_Line | Oklaunion-Fisher Road 345-kV line | 2.5
8 | GRAHAME_8_GRAHAMSW_8_138_Line | Oklaunion-Fisher Road 345-kV line | 2.4
8 | BARTON_8_ORAN1_8_138_Line | Oklaunion-Fisher Road 345-kV line | 4.6
8 | LEONSW_8_FLATCRK_T8_138_Line | Oklaunion-Fisher Road 345-kV line | 3.5
8 | LINGLVLL_P8_STPHNVIL_8_138_Line | Oklaunion-Fisher Road 345-kV line | 3.5
8 | FLATCRK_T8_LINGLVLL_P8_138_Line | Oklaunion-Fisher Road 345-kV line | 3.5
8 | PAIP4B_MURRY_P8_138_Line | Oklaunion-Fisher Road 345-kV line | 4.3
8 | BLF_CRK7A_ABMULCE7_345_Line | Oklaunion-Fisher Road 345-kV line | 7.2
9 | CSC_1 | Jacksboro-West Denton 345-kV line | 35
9 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Jacksboro-West Denton 345-kV line | 15.2
9 | MURRY_P8_GRAHAMSES1_8_138_Line | Jacksboro-West Denton 345-kV line | 4.3
9 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Jacksboro-West Denton 345-kV line | 15.4
9 | WILLOWCK_5_JACKSBRO_5_345_Line | Jacksboro-West Denton 345-kV line | -13.9
9 | WILLOWCK_5_PARKER_5_345_Line | Jacksboro-West Denton 345-kV line | 11
9 | FISHRDSS1_5_BOWMAN_5_345_Line | Jacksboro-West Denton 345-kV line | -0.1
9 | BOWMAN_5_JACKSBRO_5_345_Line | Jacksboro-West Denton 345-kV line | 5.9
9 | OKLA7A_FISHRDSS1_5_345_Line | Jacksboro-West Denton 345-kV line | 0
9 | JACKSBRO_5_W_DENT_5_345_Line | Jacksboro-West Denton 345-kV line | 10.9
9 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Jacksboro-West Denton 345-kV line | 18.8
9 | GRAHAMSES1_5_BENBRK_5_345_Line | Jacksboro-West Denton 345-kV line | 16.3
9 | GRAHAMSES1_8_GRAHAME_8_138_Line | Jacksboro-West Denton 345-kV line | 2.4
9 | LONGCREK_5_GRAHAMSES1_5_345_Line | Jacksboro-West Denton 345-kV line | 28.4
9 | ABMULCE7_LONGCREK_5_345_Line | Jacksboro-West Denton 345-kV line | 17.6
9 | PARKER_5_BENBRK_A_T5_345_Line | Jacksboro-West Denton 345-kV line | 7.6
9 | COMCHESS1_5_COMCHPKW_5_345_Line | Jacksboro-West Denton 345-kV line | 18
9 | SARC7A_COMCHESS1_5_345_Line | Jacksboro-West Denton 345-kV line | 18.3
9 | LKAROWHD_8_NEWPRT_P8_138_Line | Jacksboro-West Denton 345-kV line | 2.2
9 | GRAHAMSW_8_BARTON_8_138_Line | Jacksboro-West Denton 345-kV line | 2.5
9 | GRAHAME_8_GRAHAMSW_8_138_Line | Jacksboro-West Denton 345-kV line | 2.4
9 | BARTON_8_ORAN1_8_138_Line | Jacksboro-West Denton 345-kV line | 4.6
9 | LEONSW_8_FLATCRK_T8_138_Line | Jacksboro-West Denton 345-kV line | 3.5
9 | LINGLVLL_P8_STPHNVIL_8_138_Line | Jacksboro-West Denton 345-kV line | 3.5
9 | FLATCRK_T8_LINGLVLL_P8_138_Line | Jacksboro-West Denton 345-kV line | 3.5
9 | PAIP4B_MURRY_P8_138_Line | Jacksboro-West Denton 345-kV line | 4.3
9 | BLF_CRK7A_ABMULCE7_345_Line | Jacksboro-West Denton 345-kV line | 7.2
10 | CSC_1 | Graham-Jacksboro 345-kV line | 42.9
10 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Jacksboro 345-kV line | 13.4
10 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Jacksboro 345-kV line | 3.5
10 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Jacksboro 345-kV line | 13.4
10 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Jacksboro 345-kV line | -8.5
10 | WILLOWCK_5_PARKER_5_345_Line | Graham-Jacksboro 345-kV line | 5.6
10 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Jacksboro 345-kV line | 10.2
10 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Jacksboro 345-kV line | 16.5
10 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Jacksboro 345-kV line | 11.5
10 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Jacksboro 345-kV line | 8.1
10 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Jacksboro 345-kV line | 0
10 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Jacksboro 345-kV line | 19.5
10 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Jacksboro 345-kV line | 2.8
10 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Jacksboro 345-kV line | 22.8
10 | ABMULCE7_LONGCREK_5_345_Line | Graham-Jacksboro 345-kV line | 12
10 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Jacksboro 345-kV line | 6.1
10 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Jacksboro 345-kV line | 17.6
10 | SARC7A_COMCHESS1_5_345_Line | Graham-Jacksboro 345-kV line | 17.8
10 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Jacksboro 345-kV line | 2.6
10 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Jacksboro 345-kV line | 2.9
10 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Jacksboro 345-kV line | 2.8
10 | BARTON_8_ORAN1_8_138_Line | Graham-Jacksboro 345-kV line | 5
10 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Jacksboro 345-kV line | 3.6
10 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Jacksboro 345-kV line | 3.5
10 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Jacksboro 345-kV line | 3.5
10 | PAIP4B_MURRY_P8_138_Line | Graham-Jacksboro 345-kV line | 3.5
10 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Jacksboro 345-kV line | 8.6
11 | CSC_1 | Graham-Benbrook 345-kV line | 24.4
11 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Benbrook 345-kV line | 13.3
11 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Benbrook 345-kV line | 3.5
11 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Benbrook 345-kV line | 13.4
11 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Benbrook 345-kV line | -19.2
11 | WILLOWCK_5_PARKER_5_345_Line | Graham-Benbrook 345-kV line | 16.3
11 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Benbrook 345-kV line | 9.1
11 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Benbrook 345-kV line | 11
11 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Benbrook 345-kV line | 10.6
11 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Benbrook 345-kV line | 14
11 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Benbrook 345-kV line | 22.2
11 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Benbrook 345-kV line | 0
11 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Benbrook 345-kV line | 3
11 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Benbrook 345-kV line | 22.9
11 | ABMULCE7_LONGCREK_5_345_Line | Graham-Benbrook 345-kV line | 12
11 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Benbrook 345-kV line | 16.5
11 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Benbrook 345-kV line | 18.3
11 | SARC7A_COMCHESS1_5_345_Line | Graham-Benbrook 345-kV line | 18.5
11 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Benbrook 345-kV line | 2.9
11 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Benbrook 345-kV line | 3.2
11 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Benbrook 345-kV line | 3
11 | BARTON_8_ORAN1_8_138_Line | Graham-Benbrook 345-kV line | 5.2
11 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Benbrook 345-kV line | 3.8
11 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Benbrook 345-kV line | 3.7
11 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Benbrook 345-kV line | 3.7
11 | PAIP4B_MURRY_P8_138_Line | Graham-Benbrook 345-kV line | 3.5
11 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Benbrook 345-kV line | 8.1
12 | CSC_1 | Graham-Graham East 138-kV line | 35.6
12 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Graham East 138-kV line | 13.8
12 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Graham East 138-kV line | 3.4
12 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Graham East 138-kV line | 13.9
12 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Graham East 138-kV line | -15.2
12 | WILLOWCK_5_PARKER_5_345_Line | Graham-Graham East 138-kV line | 12.3
12 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Graham East 138-kV line | 9.2
12 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Graham East 138-kV line | 9.7
12 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Graham East 138-kV line | 10.7
12 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Graham East 138-kV line | 11.7
12 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Graham East 138-kV line | 17.2
12 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Graham East 138-kV line | 16.6
12 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Graham East 138-kV line | 0
12 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Graham East 138-kV line | 23.9
12 | ABMULCE7_LONGCREK_5_345_Line | Graham-Graham East 138-kV line | 13.1
12 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Graham East 138-kV line | 8.2
12 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Graham East 138-kV line | 16.8
12 | SARC7A_COMCHESS1_5_345_Line | Graham-Graham East 138-kV line | 17.2
12 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Graham East 138-kV line | 2.7
12 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Graham East 138-kV line | 0.8
12 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Graham East 138-kV line | 0
12 | BARTON_8_ORAN1_8_138_Line | Graham-Graham East 138-kV line | 2.8
12 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Graham East 138-kV line | 3.5
12 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Graham East 138-kV line | 3.4
12 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Graham East 138-kV line | 3.4
12 | PAIP4B_MURRY_P8_138_Line | Graham-Graham East 138-kV line | 3.4
12 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Graham East 138-kV line | 8.9
13 | CSC_1 | Long Creek-Graham 345-kV line | 30.6
13 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Long Creek-Graham 345-kV line | 18.6
13 | MURRY_P8_GRAHAMSES1_8_138_Line | Long Creek-Graham 345-kV line | 4.8
13 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Long Creek-Graham 345-kV line | 19
13 | WILLOWCK_5_JACKSBRO_5_345_Line | Long Creek-Graham 345-kV line | -14.1
13 | WILLOWCK_5_PARKER_5_345_Line | Long Creek-Graham 345-kV line | 11.2
13 | FISHRDSS1_5_BOWMAN_5_345_Line | Long Creek-Graham 345-kV line | 14.8
13 | BOWMAN_5_JACKSBRO_5_345_Line | Long Creek-Graham 345-kV line | 11.4
13 | OKLA7A_FISHRDSS1_5_345_Line | Long Creek-Graham 345-kV line | 16.7
13 | JACKSBRO_5_W_DENT_5_345_Line | Long Creek-Graham 345-kV line | 10.8
13 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Long Creek-Graham 345-kV line | 13.5
13 | GRAHAMSES1_5_BENBRK_5_345_Line | Long Creek-Graham 345-kV line | 14.3
13 | GRAHAMSES1_8_GRAHAME_8_138_Line | Long Creek-Graham 345-kV line | 2.3
13 | LONGCREK_5_GRAHAMSES1_5_345_Line | Long Creek-Graham 345-kV line | 0
13 | ABMULCE7_LONGCREK_5_345_Line | Long Creek-Graham 345-kV line | -10.8
13 | PARKER_5_BENBRK_A_T5_345_Line | Long Creek-Graham 345-kV line | 7.4
13 | COMCHESS1_5_COMCHPKW_5_345_Line | Long Creek-Graham 345-kV line | 20.5
13 | SARC7A_COMCHESS1_5_345_Line | Long Creek-Graham 345-kV line | 20.8
13 | LKAROWHD_8_NEWPRT_P8_138_Line | Long Creek-Graham 345-kV line | 2.6
13 | GRAHAMSW_8_BARTON_8_138_Line | Long Creek-Graham 345-kV line | 2.5
13 | GRAHAME_8_GRAHAMSW_8_138_Line | Long Creek-Graham 345-kV line | 2.3
13 | BARTON_8_ORAN1_8_138_Line | Long Creek-Graham 345-kV line | 4.5
13 | LEONSW_8_FLATCRK_T8_138_Line | Long Creek-Graham 345-kV line | 3.7
13 | LINGLVLL_P8_STPHNVIL_8_138_Line | Long Creek-Graham 345-kV line | 3.7
13 | FLATCRK_T8_LINGLVLL_P8_138_Line | Long Creek-Graham 345-kV line | 3.7
13 | PAIP4B_MURRY_P8_138_Line | Long Creek-Graham 345-kV line | 4.8
13 | BLF_CRK7A_ABMULCE7_345_Line | Long Creek-Graham 345-kV line | 2.5
14 | CSC_1 | Abilene Mulberry Creek-Long Creek 345-kV line | 32.5
14 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 16.4
14 | MURRY_P8_GRAHAMSES1_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 4.2
14 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 16.7
14 | WILLOWCK_5_JACKSBRO_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | -14.5
14 | WILLOWCK_5_PARKER_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 11.6
14 | FISHRDSS1_5_BOWMAN_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 12.3
14 | BOWMAN_5_JACKSBRO_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 10.6
14 | OKLA7A_FISHRDSS1_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 14
14 | JACKSBRO_5_W_DENT_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 11.1
14 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 15
14 | GRAHAMSES1_5_BENBRK_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 15.2
14 | GRAHAMSES1_8_GRAHAME_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 2.3
14 | LONGCREK_5_GRAHAMSES1_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 10.8
14 | ABMULCE7_LONGCREK_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 0
14 | PARKER_5_BENBRK_A_T5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 7.7
14 | COMCHESS1_5_COMCHPKW_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 18.8
14 | SARC7A_COMCHESS1_5_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 19.1
14 | LKAROWHD_8_NEWPRT_P8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 2.6
14 | GRAHAMSW_8_BARTON_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 2.5
14 | GRAHAME_8_GRAHAMSW_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 2.3
14 | BARTON_8_ORAN1_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 4.6
14 | LEONSW_8_FLATCRK_T8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 3.6
14 | LINGLVLL_P8_STPHNVIL_8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 3.5
14 | FLATCRK_T8_LINGLVLL_P8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 3.5
14 | PAIP4B_MURRY_P8_138_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 4.2
14 | BLF_CRK7A_ABMULCE7_345_Line | Abilene Mulberry Creek-Long Creek 345-kV line | 5.5
15 | CSC_1 | Parker-Benbrook 345-kV line | 35.4
15 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Parker-Benbrook 345-kV line | 13.8
15 | MURRY_P8_GRAHAMSES1_8_138_Line | Parker-Benbrook 345-kV line | 3.5
15 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Parker-Benbrook 345-kV line | 13.9
15 | WILLOWCK_5_JACKSBRO_5_345_Line | Parker-Benbrook 345-kV line | -13.9
15 | WILLOWCK_5_PARKER_5_345_Line | Parker-Benbrook 345-kV line | 11.1
15 | FISHRDSS1_5_BOWMAN_5_345_Line | Parker-Benbrook 345-kV line | 9.1
15 | BOWMAN_5_JACKSBRO_5_345_Line | Parker-Benbrook 345-kV line | 9.3
15 | OKLA7A_FISHRDSS1_5_345_Line | Parker-Benbrook 345-kV line | 10.6
15 | JACKSBRO_5_W_DENT_5_345_Line | Parker-Benbrook 345-kV line | 11.6
15 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Parker-Benbrook 345-kV line | 16.2
15 | GRAHAMSES1_5_BENBRK_5_345_Line | Parker-Benbrook 345-kV line | 18
15 | GRAHAMSES1_8_GRAHAME_8_138_Line | Parker-Benbrook 345-kV line | 2.4
15 | LONGCREK_5_GRAHAMSES1_5_345_Line | Parker-Benbrook 345-kV line | 23.9
15 | ABMULCE7_LONGCREK_5_345_Line | Parker-Benbrook 345-kV line | 13
15 | PARKER_5_BENBRK_A_T5_345_Line | Parker-Benbrook 345-kV line | 0
15 | COMCHESS1_5_COMCHPKW_5_345_Line | Parker-Benbrook 345-kV line | 16.9
15 | SARC7A_COMCHESS1_5_345_Line | Parker-Benbrook 345-kV line | 17.2
15 | LKAROWHD_8_NEWPRT_P8_138_Line | Parker-Benbrook 345-kV line | 2.6
15 | GRAHAMSW_8_BARTON_8_138_Line | Parker-Benbrook 345-kV line | 2.6
15 | GRAHAME_8_GRAHAMSW_8_138_Line | Parker-Benbrook 345-kV line | 2.4
15 | BARTON_8_ORAN1_8_138_Line | Parker-Benbrook 345-kV line | 4.6
15 | LEONSW_8_FLATCRK_T8_138_Line | Parker-Benbrook 345-kV line | 3.4
15 | LINGLVLL_P8_STPHNVIL_8_138_Line | Parker-Benbrook 345-kV line | 3.4
15 | FLATCRK_T8_LINGLVLL_P8_138_Line | Parker-Benbrook 345-kV line | 3.4
15 | PAIP4B_MURRY_P8_138_Line | Parker-Benbrook 345-kV line | 3.5
15 | BLF_CRK7A_ABMULCE7_345_Line | Parker-Benbrook 345-kV line | 8.9
16 | CSC_1 | Comanche Switch-Comanche Peak 345-kV line | 40.5
16 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 15.7
16 | MURRY_P8_GRAHAMSES1_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 3.9
16 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 15.9
16 | WILLOWCK_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | -17.4
16 | WILLOWCK_5_PARKER_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 14.5
16 | FISHRDSS1_5_BOWMAN_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 10.7
16 | BOWMAN_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 11.1
16 | OKLA7A_FISHRDSS1_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 12.3
16 | JACKSBRO_5_W_DENT_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 12.8
16 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 19.2
16 | GRAHAMSES1_5_BENBRK_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 19
16 | GRAHAMSES1_8_GRAHAME_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 2.6
16 | LONGCREK_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 27.5
16 | ABMULCE7_LONGCREK_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 16.6
16 | PARKER_5_BENBRK_A_T5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 9.3
16 | COMCHESS1_5_COMCHPKW_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 0
16 | SARC7A_COMCHESS1_5_345_Line | Comanche Switch-Comanche Peak 345-kV line | 7.4
16 | LKAROWHD_8_NEWPRT_P8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 2.8
16 | GRAHAMSW_8_BARTON_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 2.8
16 | GRAHAME_8_GRAHAMSW_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 2.6
16 | BARTON_8_ORAN1_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 4.8
16 | LEONSW_8_FLATCRK_T8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 3.1
16 | LINGLVLL_P8_STPHNVIL_8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 3.1
16 | FLATCRK_T8_LINGLVLL_P8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 3.1
16 | PAIP4B_MURRY_P8_138_Line | Comanche Switch-Comanche Peak 345-kV line | 3.9
16 | BLF_CRK7A_ABMULCE7_345_Line | Comanche Switch-Comanche Peak 345-kV line | 13.3
17 | CSC_1 | Red Creek-Comanche Switch 345-kV line | 41.7
17 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Red Creek-Comanche Switch 345-kV line | 16.4
17 | MURRY_P8_GRAHAMSES1_8_138_Line | Red Creek-Comanche Switch 345-kV line | 4.1
17 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Red Creek-Comanche Switch 345-kV line | 16.6
17 | WILLOWCK_5_JACKSBRO_5_345_Line | Red Creek-Comanche Switch 345-kV line | -17.8
17 | WILLOWCK_5_PARKER_5_345_Line | Red Creek-Comanche Switch 345-kV line | 15
17 | FISHRDSS1_5_BOWMAN_5_345_Line | Red Creek-Comanche Switch 345-kV line | 11.1
17 | BOWMAN_5_JACKSBRO_5_345_Line | Red Creek-Comanche Switch 345-kV line | 11.3
17 | OKLA7A_FISHRDSS1_5_345_Line | Red Creek-Comanche Switch 345-kV line | 12.8
17 | JACKSBRO_5_W_DENT_5_345_Line | Red Creek-Comanche Switch 345-kV line | 13.2
17 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Red Creek-Comanche Switch 345-kV line | 19.8
17 | GRAHAMSES1_5_BENBRK_5_345_Line | Red Creek-Comanche Switch 345-kV line | 19.5
17 | GRAHAMSES1_8_GRAHAME_8_138_Line | Red Creek-Comanche Switch 345-kV line | 3
17 | LONGCREK_5_GRAHAMSES1_5_345_Line | Red Creek-Comanche Switch 345-kV line | 28.5
17 | ABMULCE7_LONGCREK_5_345_Line | Red Creek-Comanche Switch 345-kV line | 17.7
17 | PARKER_5_BENBRK_A_T5_345_Line | Red Creek-Comanche Switch 345-kV line | 9.7
17 | COMCHESS1_5_COMCHPKW_5_345_Line | Red Creek-Comanche Switch 345-kV line | 3.8
17 | SARC7A_COMCHESS1_5_345_Line | Red Creek-Comanche Switch 345-kV line | 0
17 | LKAROWHD_8_NEWPRT_P8_138_Line | Red Creek-Comanche Switch 345-kV line | 2.9
17 | GRAHAMSW_8_BARTON_8_138_Line | Red Creek-Comanche Switch 345-kV line | 3.1
17 | GRAHAME_8_GRAHAMSW_8_138_Line | Red Creek-Comanche Switch 345-kV line | 3
17 | BARTON_8_ORAN1_8_138_Line | Red Creek-Comanche Switch 345-kV line | 5.2
17 | LEONSW_8_FLATCRK_T8_138_Line | Red Creek-Comanche Switch 345-kV line | 4.3
17 | LINGLVLL_P8_STPHNVIL_8_138_Line | Red Creek-Comanche Switch 345-kV line | 4.3
17 | FLATCRK_T8_LINGLVLL_P8_138_Line | Red Creek-Comanche Switch 345-kV line | 4.3
17 | PAIP4B_MURRY_P8_138_Line | Red Creek-Comanche Switch 345-kV line | 4.1
17 | BLF_CRK7A_ABMULCE7_345_Line | Red Creek-Comanche Switch 345-kV line | 15.1
18 | CSC_1 | Lake Arrowhead-Newport 138-kV line | 35.7
18 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Lake Arrowhead-Newport 138-kV line | 13.9
18 | MURRY_P8_GRAHAMSES1_8_138_Line | Lake Arrowhead-Newport 138-kV line | 3.5
18 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Lake Arrowhead-Newport 138-kV line | 13.9
18 | WILLOWCK_5_JACKSBRO_5_345_Line | Lake Arrowhead-Newport 138-kV line | -15.4
18 | WILLOWCK_5_PARKER_5_345_Line | Lake Arrowhead-Newport 138-kV line | 12.6
18 | FISHRDSS1_5_BOWMAN_5_345_Line | Lake Arrowhead-Newport 138-kV line | 9.5
18 | BOWMAN_5_JACKSBRO_5_345_Line | Lake Arrowhead-Newport 138-kV line | 10.4
18 | OKLA7A_FISHRDSS1_5_345_Line | Lake Arrowhead-Newport 138-kV line | 10.4
18 | JACKSBRO_5_W_DENT_5_345_Line | Lake Arrowhead-Newport 138-kV line | 11.9
18 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Lake Arrowhead-Newport 138-kV line | 17
18 | GRAHAMSES1_5_BENBRK_5_345_Line | Lake Arrowhead-Newport 138-kV line | 16.7
18 | GRAHAMSES1_8_GRAHAME_8_138_Line | Lake Arrowhead-Newport 138-kV line | 2.6
18 | LONGCREK_5_GRAHAMSES1_5_345_Line | Lake Arrowhead-Newport 138-kV line | 24
18 | ABMULCE7_LONGCREK_5_345_Line | Lake Arrowhead-Newport 138-kV line | 13.1
18 | PARKER_5_BENBRK_A_T5_345_Line | Lake Arrowhead-Newport 138-kV line | 8.2
18 | COMCHESS1_5_COMCHPKW_5_345_Line | Lake Arrowhead-Newport 138-kV line | 16.9
18 | SARC7A_COMCHESS1_5_345_Line | Lake Arrowhead-Newport 138-kV line | 17.2
18 | LKAROWHD_8_NEWPRT_P8_138_Line | Lake Arrowhead-Newport 138-kV line | 0
18 | GRAHAMSW_8_BARTON_8_138_Line | Lake Arrowhead-Newport 138-kV line | 2.8
18 | GRAHAME_8_GRAHAMSW_8_138_Line | Lake Arrowhead-Newport 138-kV line | 2.6
18 | BARTON_8_ORAN1_8_138_Line | Lake Arrowhead-Newport 138-kV line | 4.8
18 | LEONSW_8_FLATCRK_T8_138_Line | Lake Arrowhead-Newport 138-kV line | 3.4
18 | LINGLVLL_P8_STPHNVIL_8_138_Line | Lake Arrowhead-Newport 138-kV line | 3.4
18 | FLATCRK_T8_LINGLVLL_P8_138_Line | Lake Arrowhead-Newport 138-kV line | 3.4
18 | PAIP4B_MURRY_P8_138_Line | Lake Arrowhead-Newport 138-kV line | 3.5
18 | BLF_CRK7A_ABMULCE7_345_Line | Lake Arrowhead-Newport 138-kV line | 8.9
19 | CSC_1 | Graham Southwest-Barton 138-kV line | 35.7
19 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham Southwest-Barton 138-kV line | 13.9
19 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham Southwest-Barton 138-kV line | 3.5
19 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham Southwest-Barton 138-kV line | 13.9
19 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham Southwest-Barton 138-kV line | -15.4
19 | WILLOWCK_5_PARKER_5_345_Line | Graham Southwest-Barton 138-kV line | 12.6
19 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham Southwest-Barton 138-kV line | 9.5
19 | BOWMAN_5_JACKSBRO_5_345_Line | Graham Southwest-Barton 138-kV line | 10.4
19 | OKLA7A_FISHRDSS1_5_345_Line | Graham Southwest-Barton 138-kV line | 10.4
19 | JACKSBRO_5_W_DENT_5_345_Line | Graham Southwest-Barton 138-kV line | 11.9
19 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham Southwest-Barton 138-kV line | 17
19 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham Southwest-Barton 138-kV line | 16.7
19 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham Southwest-Barton 138-kV line | 2.6
19 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham Southwest-Barton 138-kV line | 24
19 | ABMULCE7_LONGCREK_5_345_Line | Graham Southwest-Barton 138-kV line | 13.1
19 | PARKER_5_BENBRK_A_T5_345_Line | Graham Southwest-Barton 138-kV line | 8.2
19 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham Southwest-Barton 138-kV line | 16.9
19 | SARC7A_COMCHESS1_5_345_Line | Graham Southwest-Barton 138-kV line | 17.2
19 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham Southwest-Barton 138-kV line | 0
19 | GRAHAMSW_8_BARTON_8_138_Line | Graham Southwest-Barton 138-kV line | 2.8
19 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham Southwest-Barton 138-kV line | 2.6
19 | BARTON_8_ORAN1_8_138_Line | Graham Southwest-Barton 138-kV line | 4.8
19 | LEONSW_8_FLATCRK_T8_138_Line | Graham Southwest-Barton 138-kV line | 3.4
19 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham Southwest-Barton 138-kV line | 3.4
19 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham Southwest-Barton 138-kV line | 3.4
19 | PAIP4B_MURRY_P8_138_Line | Graham Southwest-Barton 138-kV line | 3.5
19 | BLF_CRK7A_ABMULCE7_345_Line | Graham Southwest-Barton 138-kV line | 8.9
20 | CSC_1 | Graham East-Graham Southwest 138-kV line | 35.6
20 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham East-Graham Southwest 138-kV line | 13.8
20 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham East-Graham Southwest 138-kV line | 3.4
20 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham East-Graham Southwest 138-kV line | 13.9
20 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham East-Graham Southwest 138-kV line | -15.2
20 | WILLOWCK_5_PARKER_5_345_Line | Graham East-Graham Southwest 138-kV line | 12.3
20 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham East-Graham Southwest 138-kV line | 9.2
20 | BOWMAN_5_JACKSBRO_5_345_Line | Graham East-Graham Southwest 138-kV line | 9.7
20 | OKLA7A_FISHRDSS1_5_345_Line | Graham East-Graham Southwest 138-kV line | 10.7
20 | JACKSBRO_5_W_DENT_5_345_Line | Graham East-Graham Southwest 138-kV line | 11.7
20 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham East-Graham Southwest 138-kV line | 17.2
20 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham East-Graham Southwest 138-kV line | 16.6
20 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham East-Graham Southwest 138-kV line | 0
20 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham East-Graham Southwest 138-kV line | 23.9
20 | ABMULCE7_LONGCREK_5_345_Line | Graham East-Graham Southwest 138-kV line | 13.1
20 | PARKER_5_BENBRK_A_T5_345_Line | Graham East-Graham Southwest 138-kV line | 8.2
20 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham East-Graham Southwest 138-kV line | 16.8
20 | SARC7A_COMCHESS1_5_345_Line | Graham East-Graham Southwest 138-kV line | 17.2
20 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham East-Graham Southwest 138-kV line | 2.7
20 | GRAHAMSW_8_BARTON_8_138_Line | Graham East-Graham Southwest 138-kV line | 0.8
20 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham East-Graham Southwest 138-kV line | 0
20 | BARTON_8_ORAN1_8_138_Line | Graham East-Graham Southwest 138-kV line | 2.8
20 | LEONSW_8_FLATCRK_T8_138_Line | Graham East-Graham Southwest 138-kV line | 3.5
20 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham East-Graham Southwest 138-kV line | 3.4
20 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham East-Graham Southwest 138-kV line | 3.4
20 | PAIP4B_MURRY_P8_138_Line | Graham East-Graham Southwest 138-kV line | 3.4
20 | BLF_CRK7A_ABMULCE7_345_Line | Graham East-Graham Southwest 138-kV line | 8.9
21 | CSC_1 | Barton-Oran 138-kV line | 36.6
21 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Barton-Oran 138-kV line | 13.8
21 | MURRY_P8_GRAHAMSES1_8_138_Line | Barton-Oran 138-kV line | 3.2
21 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Barton-Oran 138-kV line | 13.9
21 | WILLOWCK_5_JACKSBRO_5_345_Line | Barton-Oran 138-kV line | -15.6
21 | WILLOWCK_5_PARKER_5_345_Line | Barton-Oran 138-kV line | 12.8
21 | FISHRDSS1_5_BOWMAN_5_345_Line | Barton-Oran 138-kV line | 9.3
21 | BOWMAN_5_JACKSBRO_5_345_Line | Barton-Oran 138-kV line | 10.1
21 | OKLA7A_FISHRDSS1_5_345_Line | Barton-Oran 138-kV line | 10.6
21 | JACKSBRO_5_W_DENT_5_345_Line | Barton-Oran 138-kV line | 12.1
21 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Barton-Oran 138-kV line | 17.6
21 | GRAHAMSES1_5_BENBRK_5_345_Line | Barton-Oran 138-kV line | 17.1
21 | GRAHAMSES1_8_GRAHAME_8_138_Line | Barton-Oran 138-kV line | -1.9
21 | LONGCREK_5_GRAHAMSES1_5_345_Line | Barton-Oran 138-kV line | 23.9
21 | ABMULCE7_LONGCREK_5_345_Line | Barton-Oran 138-kV line | 13.1
21 | PARKER_5_BENBRK_A_T5_345_Line | Barton-Oran 138-kV line | 8.4
21 | COMCHESS1_5_COMCHPKW_5_345_Line | Barton-Oran 138-kV line | 16.9
21 | SARC7A_COMCHESS1_5_345_Line | Barton-Oran 138-kV line | 17.4
21 | LKAROWHD_8_NEWPRT_P8_138_Line | Barton-Oran 138-kV line | 2.9
21 | GRAHAMSW_8_BARTON_8_138_Line | Barton-Oran 138-kV line | -2
21 | GRAHAME_8_GRAHAMSW_8_138_Line | Barton-Oran 138-kV line | -1.9
21 | BARTON_8_ORAN1_8_138_Line | Barton-Oran 138-kV line | 0
21 | LEONSW_8_FLATCRK_T8_138_Line | Barton-Oran 138-kV line | 3.8
21 | LINGLVLL_P8_STPHNVIL_8_138_Line | Barton-Oran 138-kV line | 3.8
21 | FLATCRK_T8_LINGLVLL_P8_138_Line | Barton-Oran 138-kV line | 3.8
21 | PAIP4B_MURRY_P8_138_Line | Barton-Oran 138-kV line | 3.2
21 | BLF_CRK7A_ABMULCE7_345_Line | Barton-Oran 138-kV line | 8.8
22 | CSC_1 | Leon-Flat Creek 138-kV line | 36
22 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Leon-Flat Creek 138-kV line | 13.9
22 | MURRY_P8_GRAHAMSES1_8_138_Line | Leon-Flat Creek 138-kV line | 3.5
22 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Leon-Flat Creek 138-kV line | 14
22 | WILLOWCK_5_JACKSBRO_5_345_Line | Leon-Flat Creek 138-kV line | -15.4
22 | WILLOWCK_5_PARKER_5_345_Line | Leon-Flat Creek 138-kV line | 12.5
22 | FISHRDSS1_5_BOWMAN_5_345_Line | Leon-Flat Creek 138-kV line | 9.4
22 | BOWMAN_5_JACKSBRO_5_345_Line | Leon-Flat Creek 138-kV line | 9.9
22 | OKLA7A_FISHRDSS1_5_345_Line | Leon-Flat Creek 138-kV line | 10.8
22 | JACKSBRO_5_W_DENT_5_345_Line | Leon-Flat Creek 138-kV line | 11.8
22 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Leon-Flat Creek 138-kV line | 17.3
22 | GRAHAMSES1_5_BENBRK_5_345_Line | Leon-Flat Creek 138-kV line | 16.8
22 | GRAHAMSES1_8_GRAHAME_8_138_Line | Leon-Flat Creek 138-kV line | 2.7
22 | LONGCREK_5_GRAHAMSES1_5_345_Line | Leon-Flat Creek 138-kV line | 24.2
22 | ABMULCE7_LONGCREK_5_345_Line | Leon-Flat Creek 138-kV line | 13.3
22 | PARKER_5_BENBRK_A_T5_345_Line | Leon-Flat Creek 138-kV line | 8.4
22 | COMCHESS1_5_COMCHPKW_5_345_Line | Leon-Flat Creek 138-kV line | 16.6
22 | SARC7A_COMCHESS1_5_345_Line | Leon-Flat Creek 138-kV line | 17.6
22 | LKAROWHD_8_NEWPRT_P8_138_Line | Leon-Flat Creek 138-kV line | 2.6
22 | GRAHAMSW_8_BARTON_8_138_Line | Leon-Flat Creek 138-kV line | 3
22 | GRAHAME_8_GRAHAMSW_8_138_Line | Leon-Flat Creek 138-kV line | 2.7
22 | BARTON_8_ORAN1_8_138_Line | Leon-Flat Creek 138-kV line | 5.1
22 | LEONSW_8_FLATCRK_T8_138_Line | Leon-Flat Creek 138-kV line | 0
22 | LINGLVLL_P8_STPHNVIL_8_138_Line | Leon-Flat Creek 138-kV line | 0
22 | FLATCRK_T8_LINGLVLL_P8_138_Line | Leon-Flat Creek 138-kV line | 0
22 | PAIP4B_MURRY_P8_138_Line | Leon-Flat Creek 138-kV line | 3.5
22 | BLF_CRK7A_ABMULCE7_345_Line | Leon-Flat Creek 138-kV line | 9
23 | CSC_1 | Lingleville-Stephenville 138-kV line | 36
23 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Lingleville-Stephenville 138-kV line | 13.9
23 | MURRY_P8_GRAHAMSES1_8_138_Line | Lingleville-Stephenville 138-kV line | 3.5
23 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Lingleville-Stephenville 138-kV line | 14
23 | WILLOWCK_5_JACKSBRO_5_345_Line | Lingleville-Stephenville 138-kV line | -15.4
23 | WILLOWCK_5_PARKER_5_345_Line | Lingleville-Stephenville 138-kV line | 12.5
23 | FISHRDSS1_5_BOWMAN_5_345_Line | Lingleville-Stephenville 138-kV line | 9.4
23 | BOWMAN_5_JACKSBRO_5_345_Line | Lingleville-Stephenville 138-kV line | 9.9
23 | OKLA7A_FISHRDSS1_5_345_Line | Lingleville-Stephenville 138-kV line | 10.8
23 | JACKSBRO_5_W_DENT_5_345_Line | Lingleville-Stephenville 138-kV line | 11.8
23 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Lingleville-Stephenville 138-kV line | 17.3
23 | GRAHAMSES1_5_BENBRK_5_345_Line | Lingleville-Stephenville 138-kV line | 16.8
23 | GRAHAMSES1_8_GRAHAME_8_138_Line | Lingleville-Stephenville 138-kV line | 2.7
23 | LONGCREK_5_GRAHAMSES1_5_345_Line | Lingleville-Stephenville 138-kV line | 24.2
23 | ABMULCE7_LONGCREK_5_345_Line | Lingleville-Stephenville 138-kV line | 13.3
23 | PARKER_5_BENBRK_A_T5_345_Line | Lingleville-Stephenville 138-kV line | 8.4
23 | COMCHESS1_5_COMCHPKW_5_345_Line | Lingleville-Stephenville 138-kV line | 16.6
23 | SARC7A_COMCHESS1_5_345_Line | Lingleville-Stephenville 138-kV line | 17.6
23 | LKAROWHD_8_NEWPRT_P8_138_Line | Lingleville-Stephenville 138-kV line | 2.6
23 | GRAHAMSW_8_BARTON_8_138_Line | Lingleville-Stephenville 138-kV line | 3
23 | GRAHAME_8_GRAHAMSW_8_138_Line | Lingleville-Stephenville 138-kV line | 2.7
23 | BARTON_8_ORAN1_8_138_Line | Lingleville-Stephenville 138-kV line | 5
23 | LEONSW_8_FLATCRK_T8_138_Line | Lingleville-Stephenville 138-kV line | 0
23 | LINGLVLL_P8_STPHNVIL_8_138_Line | Lingleville-Stephenville 138-kV line | 0
23 | FLATCRK_T8_LINGLVLL_P8_138_Line | Lingleville-Stephenville 138-kV line | 0
23 | PAIP4B_MURRY_P8_138_Line | Lingleville-Stephenville 138-kV line | 3.5
23 | BLF_CRK7A_ABMULCE7_345_Line | Lingleville-Stephenville 138-kV line | 9
24 | CSC_1 | Flat Creek-Lingleville 138-kV line | 36
24 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Flat Creek-Lingleville 138-kV line | 13.9
24 | MURRY_P8_GRAHAMSES1_8_138_Line | Flat Creek-Lingleville 138-kV line | 3.5
24 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Flat Creek-Lingleville 138-kV line | 14
24 | WILLOWCK_5_JACKSBRO_5_345_Line | Flat Creek-Lingleville 138-kV line | -15.4
24 | WILLOWCK_5_PARKER_5_345_Line | Flat Creek-Lingleville 138-kV line | 12.5
24 | FISHRDSS1_5_BOWMAN_5_345_Line | Flat Creek-Lingleville 138-kV line | 9.4
24 | BOWMAN_5_JACKSBRO_5_345_Line | Flat Creek-Lingleville 138-kV line | 9.9
24 | OKLA7A_FISHRDSS1_5_345_Line | Flat Creek-Lingleville 138-kV line | 10.8
24 | JACKSBRO_5_W_DENT_5_345_Line | Flat Creek-Lingleville 138-kV line | 11.8
24 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Flat Creek-Lingleville 138-kV line | 17.3
24 | GRAHAMSES1_5_BENBRK_5_345_Line | Flat Creek-Lingleville 138-kV line | 16.8
24 | GRAHAMSES1_8_GRAHAME_8_138_Line | Flat Creek-Lingleville 138-kV line | 2.7
24 | LONGCREK_5_GRAHAMSES1_5_345_Line | Flat Creek-Lingleville 138-kV line | 24.2
24 | ABMULCE7_LONGCREK_5_345_Line | Flat Creek-Lingleville 138-kV line | 13.3
24 | PARKER_5_BENBRK_A_T5_345_Line | Flat Creek-Lingleville 138-kV line | 8.4
24 | COMCHESS1_5_COMCHPKW_5_345_Line | Flat Creek-Lingleville 138-kV line | 16.6
24 | SARC7A_COMCHESS1_5_345_Line | Flat Creek-Lingleville 138-kV line | 17.6
24 | LKAROWHD_8_NEWPRT_P8_138_Line | Flat Creek-Lingleville 138-kV line | 2.6
24 | GRAHAMSW_8_BARTON_8_138_Line | Flat Creek-Lingleville 138-kV line | 3
24 | GRAHAME_8_GRAHAMSW_8_138_Line | Flat Creek-Lingleville 138-kV line | 2.7
24 | BARTON_8_ORAN1_8_138_Line | Flat Creek-Lingleville 138-kV line | 5
24 | LEONSW_8_FLATCRK_T8_138_Line | Flat Creek-Lingleville 138-kV line | 0
24 | LINGLVLL_P8_STPHNVIL_8_138_Line | Flat Creek-Lingleville 138-kV line | 0
24 | FLATCRK_T8_LINGLVLL_P8_138_Line | Flat Creek-Lingleville 138-kV line | 0
24 | PAIP4B_MURRY_P8_138_Line | Flat Creek-Lingleville 138-kV line | 3.5
24 | BLF_CRK7A_ABMULCE7_345_Line | Flat Creek-Lingleville 138-kV line | 9
25 | CSC_1 | Paint Creek-Murray 138-kV line | 34.8
25 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Paint Creek-Murray 138-kV line | 14.3
25 | MURRY_P8_GRAHAMSES1_8_138_Line | Paint Creek-Murray 138-kV line | 0
25 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Paint Creek-Murray 138-kV line | 14.4
25 | WILLOWCK_5_JACKSBRO_5_345_Line | Paint Creek-Murray 138-kV line | -14.9
25 | WILLOWCK_5_PARKER_5_345_Line | Paint Creek-Murray 138-kV line | 12.1
25 | FISHRDSS1_5_BOWMAN_5_345_Line | Paint Creek-Murray 138-kV line | 9.7
25 | BOWMAN_5_JACKSBRO_5_345_Line | Paint Creek-Murray 138-kV line | 9.6
25 | OKLA7A_FISHRDSS1_5_345_Line | Paint Creek-Murray 138-kV line | 11.4
25 | JACKSBRO_5_W_DENT_5_345_Line | Paint Creek-Murray 138-kV line | 11.5
25 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Paint Creek-Murray 138-kV line | 16.8
25 | GRAHAMSES1_5_BENBRK_5_345_Line | Paint Creek-Murray 138-kV line | 16.3
25 | GRAHAMSES1_8_GRAHAME_8_138_Line | Paint Creek-Murray 138-kV line | 2
25 | LONGCREK_5_GRAHAMSES1_5_345_Line | Paint Creek-Murray 138-kV line | 24.8
25 | ABMULCE7_LONGCREK_5_345_Line | Paint Creek-Murray 138-kV line | 14
25 | PARKER_5_BENBRK_A_T5_345_Line | Paint Creek-Murray 138-kV line | 8
25 | COMCHESS1_5_COMCHPKW_5_345_Line | Paint Creek-Murray 138-kV line | 17
25 | SARC7A_COMCHESS1_5_345_Line | Paint Creek-Murray 138-kV line | 17.4
25 | LKAROWHD_8_NEWPRT_P8_138_Line | Paint Creek-Murray 138-kV line | 2.5
25 | GRAHAMSW_8_BARTON_8_138_Line | Paint Creek-Murray 138-kV line | 2.2
25 | GRAHAME_8_GRAHAMSW_8_138_Line | Paint Creek-Murray 138-kV line | 2
25 | BARTON_8_ORAN1_8_138_Line | Paint Creek-Murray 138-kV line | 4.2
25 | LEONSW_8_FLATCRK_T8_138_Line | Paint Creek-Murray 138-kV line | 3.3
25 | LINGLVLL_P8_STPHNVIL_8_138_Line | Paint Creek-Murray 138-kV line | 3.2
25 | FLATCRK_T8_LINGLVLL_P8_138_Line | Paint Creek-Murray 138-kV line | 3.2
25 | PAIP4B_MURRY_P8_138_Line | Paint Creek-Murray 138-kV line | 0
25 | BLF_CRK7A_ABMULCE7_345_Line | Paint Creek-Murray 138-kV line | 9.1
26 | CSC_1 | Bluff Creek-Abilene Mulberry Creek 345-kV line | 33.8
26 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 14.1
26 | MURRY_P8_GRAHAMSES1_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 3.5
26 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 14.2
26 | WILLOWCK_5_JACKSBRO_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | -14.5
26 | WILLOWCK_5_PARKER_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 11.6
26 | FISHRDSS1_5_BOWMAN_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 8.6
26 | BOWMAN_5_JACKSBRO_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 9.2
26 | OKLA7A_FISHRDSS1_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 9.9
26 | JACKSBRO_5_W_DENT_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 11.2
26 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 16.5
26 | GRAHAMSES1_5_BENBRK_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 15.8
26 | GRAHAMSES1_8_GRAHAME_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 2.3
26 | LONGCREK_5_GRAHAMSES1_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 22
26 | ABMULCE7_LONGCREK_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 11.1
26 | PARKER_5_BENBRK_A_T5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 7.8
26 | COMCHESS1_5_COMCHPKW_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 18.1
26 | SARC7A_COMCHESS1_5_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 18.6
26 | LKAROWHD_8_NEWPRT_P8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 2.5
26 | GRAHAMSW_8_BARTON_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 2.5
26 | GRAHAME_8_GRAHAMSW_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 2.3
26 | BARTON_8_ORAN1_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 4.5
26 | LEONSW_8_FLATCRK_T8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 3.3
26 | LINGLVLL_P8_STPHNVIL_8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 3.3
26 | FLATCRK_T8_LINGLVLL_P8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 3.3
26 | PAIP4B_MURRY_P8_138_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 3.5
26 | BLF_CRK7A_ABMULCE7_345_Line | Bluff Creek-Abilene Mulberry Creek 345-kV line | 0
27 | CSC_1 | Graham-Long Creek 345-kV double circuit | 26.6
27 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Long Creek 345-kV double circuit | 25.8
27 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Long Creek 345-kV double circuit | 5.9
27 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Long Creek 345-kV double circuit | 0
27 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Long Creek 345-kV double circuit | -13.1
27 | WILLOWCK_5_PARKER_5_345_Line | Graham-Long Creek 345-kV double circuit | 10.2
27 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Long Creek 345-kV double circuit | 18.6
27 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Long Creek 345-kV double circuit | 12.5
27 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Long Creek 345-kV double circuit | 20.8
27 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Long Creek 345-kV double circuit | 10.1
27 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Long Creek 345-kV double circuit | 10.6
27 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Long Creek 345-kV double circuit | 12.5
27 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Long Creek 345-kV double circuit | 2.2
27 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Long Creek 345-kV double circuit | 0
27 | ABMULCE7_LONGCREK_5_345_Line | Graham-Long Creek 345-kV double circuit | -10.8
27 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Long Creek 345-kV double circuit | 6.7
27 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Long Creek 345-kV double circuit | 24.2
27 | SARC7A_COMCHESS1_5_345_Line | Graham-Long Creek 345-kV double circuit | 24.5
27 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Long Creek 345-kV double circuit | 2.6
27 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Long Creek 345-kV double circuit | 2.4
27 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Long Creek 345-kV double circuit | 2.2
27 | BARTON_8_ORAN1_8_138_Line | Graham-Long Creek 345-kV double circuit | 4.5
27 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Long Creek 345-kV double circuit | 4
27 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Long Creek 345-kV double circuit | 4
27 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Long Creek 345-kV double circuit | 4
27 | PAIP4B_MURRY_P8_138_Line | Graham-Long Creek 345-kV double circuit | 5.9
27 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Long Creek 345-kV double circuit | 2
28 | CSC_1 | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 29.1
28 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 22.8
28 | MURRY_P8_GRAHAMSES1_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 5.2
28 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 0
28 | WILLOWCK_5_JACKSBRO_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | -13.6
28 | WILLOWCK_5_PARKER_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 10.7
28 | FISHRDSS1_5_BOWMAN_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 15.6
28 | BOWMAN_5_JACKSBRO_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 11.6
28 | OKLA7A_FISHRDSS1_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 17.6
28 | JACKSBRO_5_W_DENT_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 10.5
28 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 12.5
28 | GRAHAMSES1_5_BENBRK_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 13.6
28 | GRAHAMSES1_8_GRAHAME_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 2.2
28 | LONGCREK_5_GRAHAMSES1_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 10.8
28 | ABMULCE7_LONGCREK_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 0
28 | PARKER_5_BENBRK_A_T5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 7.1
28 | COMCHESS1_5_COMCHPKW_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 22
28 | SARC7A_COMCHESS1_5_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 22.4
28 | LKAROWHD_8_NEWPRT_P8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 2.6
28 | GRAHAMSW_8_BARTON_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 2.5
28 | GRAHAME_8_GRAHAMSW_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 2.2
28 | BARTON_8_ORAN1_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 4.5
28 | LEONSW_8_FLATCRK_T8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 3.8
28 | LINGLVLL_P8_STPHNVIL_8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 3.8
28 | FLATCRK_T8_LINGLVLL_P8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 3.8
28 | PAIP4B_MURRY_P8_138_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 5.2
28 | BLF_CRK7A_ABMULCE7_345_Line | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 5
29 | CSC_1 | Mulberry Creek-Bittercreek 345-kV double circuit | 32.6
29 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 22.5
29 | MURRY_P8_GRAHAMSES1_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 4.1
29 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 0
29 | WILLOWCK_5_JACKSBRO_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | -14.1
29 | WILLOWCK_5_PARKER_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 11.3
29 | FISHRDSS1_5_BOWMAN_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 9.5
29 | BOWMAN_5_JACKSBRO_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 9.5
29 | OKLA7A_FISHRDSS1_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 10.9
29 | JACKSBRO_5_W_DENT_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 10.9
29 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 15.6
29 | GRAHAMSES1_5_BENBRK_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 15.2
29 | GRAHAMSES1_8_GRAHAME_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 2.3
29 | LONGCREK_5_GRAHAMSES1_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 24.2
29 | ABMULCE7_LONGCREK_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 13.3
29 | PARKER_5_BENBRK_A_T5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 7.5
29 | COMCHESS1_5_COMCHPKW_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 19.2
29 | SARC7A_COMCHESS1_5_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 19.7
29 | LKAROWHD_8_NEWPRT_P8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 2.5
29 | GRAHAMSW_8_BARTON_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 2.5
29 | GRAHAME_8_GRAHAMSW_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 2.3
29 | BARTON_8_ORAN1_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 4.5
29 | LEONSW_8_FLATCRK_T8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 3.4
29 | LINGLVLL_P8_STPHNVIL_8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 3.3
29 | FLATCRK_T8_LINGLVLL_P8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 3.3
29 | PAIP4B_MURRY_P8_138_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 4.1
29 | BLF_CRK7A_ABMULCE7_345_Line | Mulberry Creek-Bittercreek 345-kV double circuit | 16.5
30 | CSC_1 | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 33
30 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 18
30 | MURRY_P8_GRAHAMSES1_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 4
30 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 0
30 | WILLOWCK_5_JACKSBRO_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | -14.4
30 | WILLOWCK_5_PARKER_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 11.6
30 | FISHRDSS1_5_BOWMAN_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 10.8
30 | BOWMAN_5_JACKSBRO_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 10
30 | OKLA7A_FISHRDSS1_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 12.4
30 | JACKSBRO_5_W_DENT_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 11.1
30 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 15.5
30 | GRAHAMSES1_5_BENBRK_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 15.4
30 | GRAHAMSES1_8_GRAHAME_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 2.3
30 | LONGCREK_5_GRAHAMSES1_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 28.3
30 | ABMULCE7_LONGCREK_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 17.4
30 | PARKER_5_BENBRK_A_T5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 7.7
30 | COMCHESS1_5_COMCHPKW_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 18.6
30 | SARC7A_COMCHESS1_5_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 18.9
30 | LKAROWHD_8_NEWPRT_P8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 2.5
30 | GRAHAMSW_8_BARTON_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 2.5
30 | GRAHAME_8_GRAHAMSW_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 2.3
30 | BARTON_8_ORAN1_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 4.5
30 | LEONSW_8_FLATCRK_T8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 3.5
30 | LINGLVLL_P8_STPHNVIL_8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 3.4
30 | FLATCRK_T8_LINGLVLL_P8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 3.4
30 | PAIP4B_MURRY_P8_138_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 4
30 | BLF_CRK7A_ABMULCE7_345_Line | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 9.8
31 | CSC_1 | Sweetwater-Bittercreek 345-kV double circuit | 32.8
31 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 20.1
31 | MURRY_P8_GRAHAMSES1_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 4.1
31 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 0
31 | WILLOWCK_5_JACKSBRO_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | -14.3
31 | WILLOWCK_5_PARKER_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 11.4
31 | FISHRDSS1_5_BOWMAN_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 10.2
31 | BOWMAN_5_JACKSBRO_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 9.8
31 | OKLA7A_FISHRDSS1_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 11.7
31 | JACKSBRO_5_W_DENT_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 11
31 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 15.6
31 | GRAHAMSES1_5_BENBRK_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 15.3
31 | GRAHAMSES1_8_GRAHAME_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 2.3
31 | LONGCREK_5_GRAHAMSES1_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 26.3
31 | ABMULCE7_LONGCREK_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 15.5
31 | PARKER_5_BENBRK_A_T5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 7.6
31 | COMCHESS1_5_COMCHPKW_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 18.9
31 | SARC7A_COMCHESS1_5_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 19.3
31 | LKAROWHD_8_NEWPRT_P8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 2.5
31 | GRAHAMSW_8_BARTON_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 2.5
31 | GRAHAME_8_GRAHAMSW_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 2.3
31 | BARTON_8_ORAN1_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 4.5
31 | LEONSW_8_FLATCRK_T8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 3.4
31 | LINGLVLL_P8_STPHNVIL_8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 3.4
31 | FLATCRK_T8_LINGLVLL_P8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 3.4
31 | PAIP4B_MURRY_P8_138_Line | Sweetwater-Bittercreek 345-kV double circuit | 4.1
31 | BLF_CRK7A_ABMULCE7_345_Line | Sweetwater-Bittercreek 345-kV double circuit | 13
32 | CSC_1 | Oklaunion-Fisher Road-Bowman 345-kV line | 35
32 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 15.2
32 | MURRY_P8_GRAHAMSES1_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 4.3
32 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 15.4
32 | WILLOWCK_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | -13.9
32 | WILLOWCK_5_PARKER_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 11
32 | FISHRDSS1_5_BOWMAN_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 0
32 | BOWMAN_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 6
32 | OKLA7A_FISHRDSS1_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 0
32 | JACKSBRO_5_W_DENT_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 10.9
32 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 18.8
32 | GRAHAMSES1_5_BENBRK_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 16.3
32 | GRAHAMSES1_8_GRAHAME_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 2.4
32 | LONGCREK_5_GRAHAMSES1_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 28.4
32 | ABMULCE7_LONGCREK_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 17.6
32 | PARKER_5_BENBRK_A_T5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 7.6
32 | COMCHESS1_5_COMCHPKW_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 18
32 | SARC7A_COMCHESS1_5_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 18.3
32 | LKAROWHD_8_NEWPRT_P8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 2.2
32 | GRAHAMSW_8_BARTON_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 2.5
32 | GRAHAME_8_GRAHAMSW_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 2.4
32 | BARTON_8_ORAN1_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 4.6
32 | LEONSW_8_FLATCRK_T8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 3.5
32 | LINGLVLL_P8_STPHNVIL_8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 3.5
32 | FLATCRK_T8_LINGLVLL_P8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 3.5
32 | PAIP4B_MURRY_P8_138_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 4.3
32 | BLF_CRK7A_ABMULCE7_345_Line | Oklaunion-Fisher Road-Bowman 345-kV line | 7.2
33 | ABMULCE7_LONGCREK_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 11.6
33 | BARTON_8_ORAN1_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 5.5
33 | BLF_CRK7A_ABMULCE7_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 7.7
33 | BOWMAN_5_JACKSBRO_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 10.7
33 | COMCHESS1_5_COMCHPKW_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 18.9
33 | CSC_1 | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 23.3
33 | FISHRDSS1_5_BOWMAN_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 8.8
33 | FLATCRK_T8_LINGLVLL_P8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 4
33 | GRAHAME_8_GRAHAMSW_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.3
33 | GRAHAMSES1_5_BENBRK_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 0
33 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 21.9
33 | GRAHAMSES1_8_GRAHAME_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.3
33 | GRAHAMSW_8_BARTON_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.4
33 | JACKSBRO_5_W_DENT_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 14.8
33 | LEONSW_8_FLATCRK_T8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 4
33 | LINGLVLL_P8_STPHNVIL_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 4
33 | LKAROWHD_8_NEWPRT_P8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.1
33 | LONGCREK_5_GRAHAMSES1_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 22.4
33 | MURRY_P8_GRAHAMSES1_8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.5
33 | OKLA7A_FISHRDSS1_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 10.5
33 | PAIP4B_MURRY_P8_138_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 3.5
33 | PARKER_5_BENBRK_A_T5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 0
33 | SARC7A_COMCHESS1_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 19.1
33 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 13.2
33 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 13.1
33 | WILLOWCK_5_JACKSBRO_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | -17.9
33 | WILLOWCK_5_PARKER_5_345_Line | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 15
34 | ABMULCE7_LONGCREK_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 16.9
34 | BARTON_8_ORAN1_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 4.8
34 | BLF_CRK7A_ABMULCE7_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 13.5
34 | BOWMAN_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 11.2
34 | COMCHESS1_5_COMCHPKW_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 0
34 | CSC_1 | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 41.1
34 | FISHRDSS1_5_BOWMAN_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 10.8
34 | FLATCRK_T8_LINGLVLL_P8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.6
34 | GRAHAME_8_GRAHAMSW_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.6
34 | GRAHAMSES1_5_BENBRK_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 19.3
34 | GRAHAMSES1_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 19.4
34 | GRAHAMSES1_8_GRAHAME_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.6
34 | GRAHAMSW_8_BARTON_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.8
34 | JACKSBRO_5_W_DENT_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 13
34 | LEONSW_8_FLATCRK_T8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.6
34 | LINGLVLL_P8_STPHNVIL_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.6
34 | LKAROWHD_8_NEWPRT_P8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 2.8
34 | LONGCREK_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 27.7
34 | MURRY_P8_GRAHAMSES1_8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 3.9
34 | OKLA7A_FISHRDSS1_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 12.4
34 | PAIP4B_MURRY_P8_138_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 3.9
34 | PARKER_5_BENBRK_A_T5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 9.6
34 | SARC7A_COMCHESS1_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 7
34 | SWEETWTR_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 16.1
34 | TONKAWAWI_5_GRAHAMSES1_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 15.9
34 | WILLOWCK_5_JACKSBRO_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | -17.7
34 | WILLOWCK_5_PARKER_5_345_Line | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 14.8

## N-H PTDFs
Contingency # | Element | Contingency | PTDF | Top 3 plants with the highest impact in each direction
Base Case | CSC_4 | Base Case | 34
Base Case | GIBN_CREK_5_OBRIEN__345A_345_Line | Base Case | 16.1 | Gibbons Creek | 23.4505 | Texas A&M | 20.0151 | Atkins | 19.4219 | WA Parish | -11.0916 | Brazos Valley | -11.0814 | Dow | -9.3196
Base Case | JEWETT_N5_TOMBAL__345B_345_Line | Base Case | 18 | Limestone | 10.4247 | Big Brown | 10.1044 | Freestone Energy | 9.9895 | Channel Energy | -11.9716 | Channelview | -11.9716 | Greens Bayou | -11.3814
Base Case | JEWETT_S5_T_H_W___345B_345_Line | Base Case | 17.9 | Big Brown | 9.7654 | Freestone Energy | 9.655 | Limestone | 9.567 | TH Wharton | -13.4195 | Greens Bayou | -10.333 | Cedar Bayou | -9.9351
Base Case | KUYDAL745005_KING____345A_345_Line | Base Case | 11.5 | Big Brown | 4.9008 | Limestone | 4.8908 | Freestone Energy | 4.8418 | Channelview | -14.1513 | Channel Energy | -14.1513 | Baytown Energy | -11.0446
Base Case | KUYDAL755010_KING____345A_345_Line | Base Case | 15.3 | Frontier | 31.3407 | Gibbons Creek | 20.3398 | Texas A&M | 17.2919 | Channel Energy | -13.9175 | Channelview | -13.9175 | Baytown Energy | -11.7731
Base Case | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Base Case | 1.2 | Fayette Power | 3.4575 | Sim Gideon | 3.2042 | Lost Pines | 2.7426 | Channelview | -1.7938 | Channel Energy | -1.7938 | Greens Bayou | -1.7218
Base Case | ROANS___345C_KUYDAL755010_345_Line | Base Case | 15.3 | Frontier | 31.4472 | Gibbons Creek | 20.4463 | Texas A&M | 17.3984 | Channelview | -13.811 | Channel Energy | -13.811 | Baytown Energy | -11.6666
Base Case | TOMBAL__345B_KUYDAL745005_345_Line | Base Case | 11.5 | Big Brown | 4.9718 | Limestone | 4.9618 | Freestone Energy | 4.9128 | Channelview | -14.0803 | Channel Energy | -14.0803 | Baytown Energy | -10.9737
1 | CSC_4 | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 0
1 | GIBN_CREK_5_OBRIEN__345A_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 0
1 | JEWETT_N5_TOMBAL__345B_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 26.8 | Limestone | 15.5613 | Big Brown | 14.8832 | Freestone Energy | 14.7261 | Channel Energy | -15.8129 | Channelview | -15.8129 | Greens Bayou | -15.6197
1 | JEWETT_S5_T_H_W___345B_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 0
1 | KUYDAL745005_KING____345A_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 15.9 | Limestone | 7.4568 | Big Brown | 7.3206 | Freestone Energy | 7.2392 | Channelview | -16.1602 | Channel Energy | -16.1602 | Baytown Energy | -13.2502
1 | KUYDAL755010_KING____345A_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 28.3 | Frontier | 39.8405 | Gibbons Creek | 31.5664 | Texas A&M | 27.3127 | Channel Energy | -19.0321 | Channelview | -19.0321 | Baytown Energy | -17.6672
1 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 1.6 | Fayette Power | 3.3976 | Sim Gideon | 3.1718 | Lost Pines | 2.7121 | Channelview | -2.0004 | Channel Energy | -2.0004 | Greens Bayou | -1.9459
1 | ROANS___345C_KUYDAL755010_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 28.3 | Frontier | 39.9469 | Gibbons Creek | 31.6729 | Texas A&M | 27.4192 | Channel Energy | -18.9256 | Channelview | -18.9256 | Baytown Energy | -17.5607
1 | TOMBAL__345B_KUYDAL745005_345_Line | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 15.9 | Limestone | 7.5278 | Big Brown | 7.3916 | Freestone Energy | 7.3102 | Channelview | -16.0892 | Channel Energy | -16.0892 | Baytown Energy | -13.1792
2 | CSC_4 | Gibbons Creek-Obrien 345-kV line | 20.7
2 | GIBN_CREK_5_OBRIEN__345A_345_Line | Gibbons Creek-Obrien 345-kV line | 0
2 | JEWETT_N5_TOMBAL__345B_345_Line | Gibbons Creek-Obrien 345-kV line | 20.6
2 | JEWETT_S5_T_H_W___345B_345_Line | Gibbons Creek-Obrien 345-kV line | 20.7
2 | KUYDAL745005_KING____345A_345_Line | Gibbons Creek-Obrien 345-kV line | 12.5
2 | KUYDAL755010_KING____345A_345_Line | Gibbons Creek-Obrien 345-kV line | 21.9
2 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Gibbons Creek-Obrien 345-kV line | 1.3
2 | ROANS___345C_KUYDAL755010_345_Line | Gibbons Creek-Obrien 345-kV line | 21.9
2 | TOMBAL__345B_KUYDAL745005_345_Line | Gibbons Creek-Obrien 345-kV line | 12.5
3 | CSC_4 | Jewett-TH Wharton 345-kV line | 20.2
3 | GIBN_CREK_5_OBRIEN__345A_345_Line | Jewett-TH Wharton 345-kV line | 20.2
3 | JEWETT_N5_TOMBAL__345B_345_Line | Jewett-TH Wharton 345-kV line | 22.4
3 | JEWETT_S5_T_H_W___345B_345_Line | Jewett-TH Wharton 345-kV line | 0
3 | KUYDAL745005_KING____345A_345_Line | Jewett-TH Wharton 345-kV line | 14
3 | KUYDAL755010_KING____345A_345_Line | Jewett-TH Wharton 345-kV line | 19
3 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Jewett-TH Wharton 345-kV line | 1.5
3 | ROANS___345C_KUYDAL755010_345_Line | Jewett-TH Wharton 345-kV line | 19
3 | TOMBAL__345B_KUYDAL745005_345_Line | Jewett-TH Wharton 345-kV line | 14
4 | CSC_4 | Jewett-Tomball 345-kV line | 42
4 | GIBN_CREK_5_OBRIEN__345A_345_Line | Jewett-Tomball 345-kV line | 19.8
4 | JEWETT_N5_TOMBAL__345B_345_Line | Jewett-Tomball 345-kV line | 0
4 | JEWETT_S5_T_H_W___345B_345_Line | Jewett-Tomball 345-kV line | 22.2
4 | KUYDAL745005_KING____345A_345_Line | Jewett-Tomball 345-kV line | 0.6
4 | KUYDAL755010_KING____345A_345_Line | Jewett-Tomball 345-kV line | 20.1
4 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Jewett-Tomball 345-kV line | 1.9
4 | ROANS___345C_KUYDAL755010_345_Line | Jewett-Tomball 345-kV line | 20.1
4 | TOMBAL__345B_KUYDAL745005_345_Line | Jewett-Tomball 345-kV line | 0.6
5 | CSC_4 | Waller-Prairie View 138-kV line | 34.1
5 | GIBN_CREK_5_OBRIEN__345A_345_Line | Waller-Prairie View 138-kV line | 16.1
5 | JEWETT_N5_TOMBAL__345B_345_Line | Waller-Prairie View 138-kV line | 18.1
5 | JEWETT_S5_T_H_W___345B_345_Line | Waller-Prairie View 138-kV line | 17.9
5 | KUYDAL745005_KING____345A_345_Line | Waller-Prairie View 138-kV line | 11.3
5 | KUYDAL755010_KING____345A_345_Line | Waller-Prairie View 138-kV line | 15.4
5 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Waller-Prairie View 138-kV line | 0
5 | ROANS___345C_KUYDAL755010_345_Line | Waller-Prairie View 138-kV line | 15.4
5 | TOMBAL__345B_KUYDAL745005_345_Line | Waller-Prairie View 138-kV line | 11.3
6 | CSC_4 | Roans Prairie-Kuykendahl 345-kV line | 43
6 | GIBN_CREK_5_OBRIEN__345A_345_Line | Roans Prairie-Kuykendahl 345-kV line | 22.6
6 | JEWETT_N5_TOMBAL__345B_345_Line | Roans Prairie-Kuykendahl 345-kV line | 21.4
6 | JEWETT_S5_T_H_W___345B_345_Line | Roans Prairie-Kuykendahl 345-kV line | 20.4
6 | KUYDAL745005_KING____345A_345_Line | Roans Prairie-Kuykendahl 345-kV line | 14.8
6 | KUYDAL755010_KING____345A_345_Line | Roans Prairie-Kuykendahl 345-kV line | 0
6 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Roans Prairie-Kuykendahl 345-kV line | 1.4
6 | ROANS___345C_KUYDAL755010_345_Line | Roans Prairie-Kuykendahl 345-kV line | 0
6 | TOMBAL__345B_KUYDAL745005_345_Line | Roans Prairie-Kuykendahl 345-kV line | 14.8
7 | CSC_4 | Kuykendahl-King 345-kV line, ckt 74 | 35.4
7 | GIBN_CREK_5_OBRIEN__345A_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 16.6
7 | JEWETT_N5_TOMBAL__345B_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 14.2
7 | JEWETT_S5_T_H_W___345B_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 18.7
7 | KUYDAL745005_KING____345A_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 0
7 | KUYDAL755010_KING____345A_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 17
7 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Kuykendahl-King 345-kV line, ckt 74 | 0.9
7 | ROANS___345C_KUYDAL755010_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 17
7 | TOMBAL__345B_KUYDAL745005_345_Line | Kuykendahl-King 345-kV line, ckt 74 | 0
8 | CSC_4 | Kuykendahl-King 345-kV line, ckt 75 | 43
8 | GIBN_CREK_5_OBRIEN__345A_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 22.6
8 | JEWETT_N5_TOMBAL__345B_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 21.4
8 | JEWETT_S5_T_H_W___345B_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 20.4
8 | KUYDAL745005_KING____345A_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 14.8
8 | KUYDAL755010_KING____345A_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 0
8 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Kuykendahl-King 345-kV line, ckt 75 | 1.4
8 | ROANS___345C_KUYDAL755010_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 0
8 | TOMBAL__345B_KUYDAL745005_345_Line | Kuykendahl-King 345-kV line, ckt 75 | 14.8
9 | CSC_4 | Tomball-Kuykendahl 345-kV line | 35.4
9 | GIBN_CREK_5_OBRIEN__345A_345_Line | Tomball-Kuykendahl 345-kV line | 16.6
9 | JEWETT_N5_TOMBAL__345B_345_Line | Tomball-Kuykendahl 345-kV line | 14.2
9 | JEWETT_S5_T_H_W___345B_345_Line | Tomball-Kuykendahl 345-kV line | 18.7
9 | KUYDAL745005_KING____345A_345_Line | Tomball-Kuykendahl 345-kV line | 0
9 | KUYDAL755010_KING____345A_345_Line | Tomball-Kuykendahl 345-kV line | 17
9 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Tomball-Kuykendahl 345-kV line | 0.9
9 | ROANS___345C_KUYDAL755010_345_Line | Tomball-Kuykendahl 345-kV line | 17
9 | TOMBAL__345B_KUYDAL745005_345_Line | Tomball-Kuykendahl 345-kV line | 0
10 | CSC_4 | Gibbons Creek-Roans Prairie 345-kV double circuit | 27.1
10 | GIBN_CREK_5_OBRIEN__345A_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 0
10 | JEWETT_N5_TOMBAL__345B_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 28.4
10 | JEWETT_S5_T_H_W___345B_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 27.1
10 | KUYDAL745005_KING____345A_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 19
10 | KUYDAL755010_KING____345A_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 0
10 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 1.7
10 | ROANS___345C_KUYDAL755010_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 0
10 | TOMBAL__345B_KUYDAL745005_345_Line | Gibbons Creek-Roans Prairie 345-kV double circuit | 19
11 | CSC_4 | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 20.6
11 | GIBN_CREK_5_OBRIEN__345A_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 0
11 | JEWETT_N5_TOMBAL__345B_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 20.6
11 | JEWETT_S5_T_H_W___345B_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 20.6
11 | KUYDAL745005_KING____345A_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 12.4
11 | KUYDAL755010_KING____345A_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 21.8
11 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 1.3
11 | ROANS___345C_KUYDAL755010_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 21.8
11 | TOMBAL__345B_KUYDAL745005_345_Line | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 12.4
12 | CSC_4 | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 26.4
12 | GIBN_CREK_5_OBRIEN__345A_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 26.4
12 | JEWETT_N5_TOMBAL__345B_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 0
12 | JEWETT_S5_T_H_W___345B_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 0
12 | KUYDAL745005_KING____345A_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 0.5
12 | KUYDAL755010_KING____345A_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 26.5
12 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 2.5
12 | ROANS___345C_KUYDAL755010_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 26.5
12 | TOMBAL__345B_KUYDAL745005_345_Line | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 0.5
13 | CSC_4 | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 20
13 | GIBN_CREK_5_OBRIEN__345A_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 20
13 | JEWETT_N5_TOMBAL__345B_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 22.5
13 | JEWETT_S5_T_H_W___345B_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 0
13 | KUYDAL745005_KING____345A_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 14.1
13 | KUYDAL755010_KING____345A_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 19.1
13 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 1.5
13 | ROANS___345C_KUYDAL755010_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 19.1
13 | TOMBAL__345B_KUYDAL745005_345_Line | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 14.1
14 | CSC_4 | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 56.8
14 | GIBN_CREK_5_OBRIEN__345A_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 29.9
14 | JEWETT_N5_TOMBAL__345B_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 0
14 | JEWETT_S5_T_H_W___345B_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 26.9
14 | KUYDAL745005_KING____345A_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 2.4
14 | KUYDAL755010_KING____345A_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 0
14 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 2.4
14 | ROANS___345C_KUYDAL755010_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 0
14 | TOMBAL__345B_KUYDAL745005_345_Line | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 2.4
15 | CSC_4 | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 42
15 | GIBN_CREK_5_OBRIEN__345A_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 19.8
15 | JEWETT_N5_TOMBAL__345B_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 0
15 | JEWETT_S5_T_H_W___345B_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 22.2
15 | KUYDAL745005_KING____345A_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 0
15 | KUYDAL755010_KING____345A_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 20.2
15 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 1.9
15 | ROANS___345C_KUYDAL755010_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 20.2
15 | TOMBAL__345B_KUYDAL745005_345_Line | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 0
16 | CSC_4 | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 56.8
16 | GIBN_CREK_5_OBRIEN__345A_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 29.9
16 | JEWETT_N5_TOMBAL__345B_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 0
16 | JEWETT_S5_T_H_W___345B_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 26.9
16 | KUYDAL745005_KING____345A_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 2.4
16 | KUYDAL755010_KING____345A_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 0
16 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 2.4
16 | ROANS___345C_KUYDAL755010_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 0
16 | TOMBAL__345B_KUYDAL745005_345_Line | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 2.4
17 | CSC_4 | King-Kuykendahl 345-kV double circuit | 46.2
17 | GIBN_CREK_5_OBRIEN__345A_345_Line | King-Kuykendahl 345-kV double circuit | 24.2
17 | JEWETT_N5_TOMBAL__345B_345_Line | King-Kuykendahl 345-kV double circuit | 16.8
17 | JEWETT_S5_T_H_W___345B_345_Line | King-Kuykendahl 345-kV double circuit | 21.9
17 | KUYDAL745005_KING____345A_345_Line | King-Kuykendahl 345-kV double circuit | 0
17 | KUYDAL755010_KING____345A_345_Line | King-Kuykendahl 345-kV double circuit | 0
17 | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | King-Kuykendahl 345-kV double circuit | 1
17 | ROANS___345C_KUYDAL755010_345_Line | King-Kuykendahl 345-kV double circuit | 0
17 | TOMBAL__345B_KUYDAL745005_345_Line | King-Kuykendahl 345-kV double circuit | 0

## N-S & S-N Contingencies
Contingency # | Contingency Name | From Bus | To Bus | Ckt | From Bus | To Bus | Ckt
1 | Temple-Sandow double circuit 345-kV line [CSC] | 3413 | 3429 | 1 | 3414 | 3429 | 1
2 | Brownwood-Goldthwaite 138-kV line | 1655 | 7070 | 1
3 | Tradinghouse-Lake Creek 345-kV line, ckt 1 | 3405 | 3409 | 1
4 | Lake Creek-Temple 345-kV line | 3409 | 3414 | 1
5 | Lake Creek-Temple Pecan 138-kV line | 3410 | 3420 | 1
6 | Tradinghouse-Temple Pecan 345-kV line | 3405 | 3412 | 1
7 | Temple Pecan-Temple 345-kV line | 3412 | 3414 | 1
8 | Temple-Rogers 138-kV line | 3415 | 3675 | 1
9 | Temple Pecan-Temple 138-kV line | 3420 | 3415 | 1
10 | Sandow-Elgin 138-kV line | 3430 | 3650 | 1
11 | Sandow-Salty 138-kV line | 3430 | 3661 | 1
12 | Sandow-Austrop 345-kV line, ckt 1 | 3429 | 7040 | 1
13 | Austrop-Zorn 345-kV line | 7040 | 7045 | 1
14 | Austrop-Garfield 345-kV line | 7040 | 7048 | 1
15 | Sandow-Austrop 345-kV line, ckt 2 | 13429 | 7040 | 2
16 | Evant-Adamsville 138-kV line | 7068 | 7066 | 1
17 | Goldthwaite-Evant 138-kV line | 7070 | 7068 | 1
18 | Rogers-Sandow 138-kV line | 3675 | 13430 | 1
19 | Tradinghouse-Lake Creek 345-kV line, ckt 2 | 3405 | 3402 | 2
20 | Tradinghouse-Lake Creek 345-kV double circuit | 3405 | 3409 | 1 | 3405 | 3412 | 1
21 | Lake Creek-Temple Pecan 345-kV double circuit | 3409 | 3414 | 1 | 3405 | 3412 | 1
22 | Temple Pecan-Temple 345-kV double circuit | 3412 | 3414 | 1 | 3409 | 3414 | 1
23 | Sandow-Austrop 345-kV double circuit | 3429 | 7040 | 1 | 13429 | 7040 | 2
24 | Austrop-Garfield 345-kV double circuit | 7040 | 7048 | 1 | 7040 | 7045 | 1
25 | Garfield-Lytton 345-kV double circuit | 7040 | 7045 | 1 | 7048 | 9074 | 1
26 | Lytton-Zorn 345-kV double circuit | 7040 | 7045 | 1 | 7042 | 9074 | 1

## W-N & N-W Contingencies
Contingency # | Contingency Name | From Bus | To Bus | Ckt | From Bus | To Bus | Ckt
1 | Graham-Parker/ Graham-Benbrook 345-kV double circuit [CSC] | 1430 | 1436 | 1 | 1430 | 1873 | 1
2 | Tonkawa-Graham 345-kV line | 1048 | 1430 | 1
3 | Murray-Graham 138-kV line | 1371 | 1431 | 1
4 | Sweetwater-Graham 345-kV line | 1420 | 1430 | 1
5 | Willow Creek-Jacksboro 345-kV line | 1421 | 1429 | 1
6 | Willow Creek-Parker 345-kV line | 1421 | 1436 | 1
7 | Bowman-Jacksboro 345-kV line | 1422 | 1429 | 1
8 | Oklaunion-Fisher Road 345-kV line | 6100 | 1425 | 1
9 | Jacksboro-West Denton 345-kV line | 1429 | 988 | 1
10 | Graham-Jacksboro 345-kV line | 1430 | 1429 | 1
11 | Graham-Benbrook 345-kV line | 1430 | 1873 | 1
12 | Graham-Graham East 138-kV line | 1431 | 1601 | 1
13 | Long Creek-Graham 345-kV line | 1435 | 1430 | 1
14 | Abilene Mulberry Creek-Long Creek 345-kV line | 6230 | 1435 | 1
15 | Parker-Benbrook 345-kV line | 1436 | 1869 | 1
16 | Comanche Switch-Comanche Peak 345-kV line | 1440 | 1900 | 1
17 | Red Creek-Comanche Switch 345-kV line | 6444 | 1440 | 1
18 | Lake Arrowhead-Newport 138-kV line | 1468 | 1470 | 1
19 | Graham Southwest-Barton 138-kV line | 1596 | 1599 | 1
20 | Graham East-Graham Southwest 138-kV line | 1601 | 1596 | 1
21 | Barton-Oran 138-kV line | 1599 | 1571 | 1
22 | Leon-Flat Creek 138-kV line | 1624 | 1642 | 1
23 | Lingleville-Stephenville 138-kV line | 1640 | 1641 | 1
24 | Flat Creek-Lingleville 138-kV line | 1642 | 1640 | 1
25 | Paint Creek-Murray 138-kV line | 6169 | 1371 | 1
26 | Bluff Creek-Abilene Mulberry Creek 345-kV line | 60040 | 6230 | 1
27 | Graham-Long Creek 345-kV double circuit | 1435 | 1430 | 1 | 1420 | 1430 | 1
28 | Long Creek-Abilene Mulberry Creek 345-kV double circuit | 6230 | 1435 | 1 | 1420 | 1430 | 1
29 | Mulberry Creek-Bittercreek 345-kV double circuit | 1050 | 6235 | 1 | 1420 | 1430 | 1
30 | Sweetwater-Morgan Creek/ Sweetwater-Graham 345-kV double circuit | 1030 | 1420 | 1 | 1420 | 1430 | 1
31 | Sweetwater-Bittercreek 345-kV double circuit | 1030 | 1050 | 1 | 1420 | 1430 | 1
32 | Oklaunion-Fisher Road-Bowman 345-kV line | 1425 | 1422 | 1 | 6100 | 1425 | 1
33 | Graham-Benbrook/ Parker-Benbrook 345-kV double circuit | 1430 | 1873 | 1 | 1436 | 1869 | 1
34 | Comanche Switch-Comanche Peak 345-kV / 138-kV double circuit | 1440 | 1900 | 1 | 1641 | 2278 | 1

## N-H Contingencies
Contingency # | Contingency Name | From Bus | To Bus | Ckt | From Bus | To Bus | Ckt
1 | Gibbons Creek-Obrien/ Jewett-TH Wharton 345-kV double circuit | 967 | 44500 | 99 | 3390 | 45500 | 1
2 | Gibbons Creek-Obrien 345-kV line | 967 | 44500 | 99
3 | Jewett-TH Wharton 345-kV line | 3390 | 45500 | 1
4 | Jewett-Tomball 345-kV line | 3391 | 46500 | 1
5 | Waller-Prairie View 138-kV line | 7272 | 7668 | 1
6 | Roans Prairie-Kuykendahl 345-kV line | 40600 | 45972 | 75
7 | Kuykendahl-King 345-kV line, ckt 74 | 45971 | 40900 | 74
8 | Kuykendahl-King 345-kV line, ckt 75 | 45972 | 40900 | 75
9 | Tomball-Kuykendahl 345-kV line | 46500 | 45971 | 74
10 | Gibbons Creek-Roans Prairie 345-kV double circuit | 967 | 44500 | 99 | 967 | 40600 | 75
11 | Obrien-Gibbons Creek/ Obrien-TH Wharton 345-kV double circuit | 967 | 44500 | 99 | 44500 | 45500 | 98
12 | Jewett-TH Wharton/ Jewett-Tomball 345-kV double circuit | 3390 | 45500 | 1 | 3391 | 46500 | 1
13 | TH Wharton-Jewett/ TH Wharton-Obrien 345-kV double circuit | 3390 | 45500 | 1 | 44500 | 45500 | 98
14 | Jewett-Tomball/ Roans Prairie-Kuykendahl 345-kV line | 3391 | 46500 | 1 | 40600 | 45972 | 75
15 | Tomball-Jewett/ Tomball-Kuykendahl 345-kV line | 3391 | 46500 | 1 | 46500 | 45971 | 64
16 | Jewett-Tomball/ Gibbons Creek-Roans Prairie 345-kV double circuit | 3391 | 46500 | 1 | 967 | 40600 | 75
17 | King-Kuykendahl 345-kV double circuit | 45971 | 40900 | 74 | 45972 | 40900 | 75