Summary Table of State Estimator and Telemetry Reports for EDS 2

TPTF members,

As a follow-up item for the EDS Update (Agenda Item 15) delivered during the recent June 9-10 TPTF Meeting, below is a summary of the State Estimator and Telemetry reports that will be published to the MIS in support of EDS 2 Release 3.

The table below provides the report name, a brief description of the report, a target date for posting to the MIS, comments regarding the period covered by the report and status of ERCOT validation efforts, and the target URL. Please note that most of the reports have not been validated and we ask Market Participants to assist with the validation of the data.

Comments on the reports should be provided to eds2data@ercot.com.

Regards,

Daryl Cote

EDS Project Manager

| Report Name | Brief Description | Target Date for deployment to EDS | Comments | MIS Locations |
| --- | --- | --- | --- | --- |
| State Estimator Statistics Extract | This extract contains the raw state estimator statistics results from the ERCOT source system, ownership information, and categorized elements used in the production of the State Estimator Statistics Reports. | 6/20 | Report will be for May ’08; not verified | State Estimator Statistics Extract |
| SE Convergence Rate Report | ERCOT will use ‘SE Convergence Rate’ reporting to track the State Estimator’s monthly convergence goal of 97% . | 6/20 | Report will be for May ’08; mostly verified | State Estimator Convergence Rate Reports |
| SE Performance – MW Residuals SE Vs Telemetry for Congested Transmission Element Reports | In order to analyze congestion and pinpoint possible errors in the network model, ERCOT will use this report to identify situations where Congested Transmission Elements are out of compliance (differences between the Mw telemetry values and MW SE values are <3% on at least 95% of samples measured in a one month period for predetermined congestion elements). | 6/20 | Report will be for May ’08 ; not verified | SE Performance MW Residuals SE vs Telemetry for Congested Transmission Element |
| Electrical Buses Not Meeting Telemetry Accuracy Requirements | In order to ensure that data received from TSP’s and QSE’s are in compliance with TAC approved standards, ERCOT will use ‘Electrical Buses Not Meeting Accuracy Requirements’ reporting to verify that TSP’s and QSE’s have maintained the sum of flows into any telemetered bus less than the greater of 5 Mw or 5% of the largest line rating at each bus. This reporting will enable the ERCOT to track and research quality issues by month throughout 2 years of history. | 6/20 | Report will be for May ’08 ; not verified | Electrical Buses Not Meeting Telemetry Accuracy Requirements |
| SE Performance – MW Residuals SE Vs RTCA Base case for Congested Transmission Element Reports | ERCOT will use this report to ensure that the residual difference between SE results and Power Flow results for congestion elements is less than 3% of the associated element emergency rating on at least 95% of samples measured in a one month trial. | TBD | No data captured in EDW yet. SPR5022 needs to be corrected. Report will not be available for at least 1 ½ months | SE Performance MW Residuals SE vs RTCA Base Case for Congested Transmission Element |
| SE Performance – MW Residuals SE Vs Telemetry for Major Transmission Elements Reports | ERCOT will use this report to ensure that all SCADA residuals (SE MW – SCADA) for all Transmission Elements over 100kV are <10% of emergency rating or <10Mw (whichever is greater) on 99.5% of all elements during a 30 day period. This reporting will enable the ERCOT to report equipment repair needs to TSP’s and QSE’s. | 6/20 | Report will be for May ’08; not verified | SE Performance MW Residuals SE vs Telemetry for Major Transmission Element |
| SE Performance – Voltage Residuals SE Vs Telemetry for Critical Buses Reports | ERCOT will use this report to ensure that for all Critical buses, telemetered bus voltage minus state estimator voltage falls within the greater of 2% accuracy or the accuracy of the telemetered voltage measurement involved for at least 95% of samples measured during a one month period. This reporting will enable the ERCOT to identify issues with the network model and telemetry received from the market participants. | 6/20 | Report will be for May ’08; not verified | SE Performance MW Residuals SE vs Telemetry for Critical Buses (note this link name will be corrected to: SE Performance – Voltage Residuals SE Vs Telemetry for Critical Buses Reports) |
| Critical Data Availability Statistics Report | ERCOT will use ‘Critical Points Violating Quarterly Availability Standards’ reporting to verify that: "Ninety five (95%) percent of the critically important telemetry defined by ERCOT must achieve a quarterly availability of ninety (90%) percent. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with valid or manual quality codes at the scheduled periodicity." ( TAC0706060-Telemetry_Standards.doc) | Mid-July | Have captured 2 of 3 months of data. Need to capture June | Critical Data Availability Statistics |
| Monthly Market Participant Real Time Availability Statistics Report | "Ninety eight (98%) percent of all telemetry provided to ERCOT must achieve a quarterly availability of eighty (80%) percent. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with good quality codes at the scheduled periodicity." - (TAC0706060-Telemetry_Standards.doc) | 6/20 | Report will be for May ’08; not verified | Monthly Market Participant Real Time Availability Statistics |
| Quarterly Point Availability Statistics Report | ERCOT will use ‘Quarterly Point Availability Statistics’ reporting to verify that Each point achieves a quarterly availability of at least 80%. This report will enable ERCOT to evaluate the availability and quality of each telemetered measurement | Mid-July | Have captured 2 of 3 months of data. Need to capture June | Quarterly Point Availability Statistics |
| ICCP Link Availability Statistics Report | "ICCP links must achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. A link will be considered as available when at least eighty-five (85%) percent of the data defined on that link is successfully transferred to ERCOT with a valid or manual quality code. This will include establishing a process to coordinate downtime for ICCP links and database maintenance." - (TAC0706060-Telemetry_Standards.doc) | 6/20 | Report will be for May ’08; not verified | Link will be added to MIS |