## N-S
North to South CSC
4 |  |  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r
|  | Overloaded Element (Where Green Cell = From Direction) | Brownwood Switch 138 1655 | Evant 138 7068 | Goldthwaite 138 7070 | Lake Creek 138 3410 | Sandow 138 3430 | Sandow Switch 138 13430 | Sandow Switch 138 3430 | Temple Pecan Creek 138 3420 | Temple Switch 138 3415 | Waco Woodway 138 3591 | Garfield 345 7048 | Sandow Switch 345 3429 | Sandow Switch 345 13429 | Zorn 345 7045 | Temple SS 345 3414 | Tradinghouse 345 3405 | Temple Switch 345 3414 | Tradinghouse 345 3405
| Contingency |  | Goldthwaite 138 7070 | Adamsville 138 7066 | Evant 138 7068 | Temple Pecan Creek 138 3420 | Elgin 138 3650 | Rogers 138 3675 | Salty 138 3661 | Temple Switch 138 3415 | Rogers 138 3675 | Waco West 138 3436 | Austrop 345 7040 | Austrop 345 7040 | Austrop 345 7040 | Austrop 345 7040 | Lake Creek 345 3409 | Lake Creek 345 3409 | Temple Pecan Creek 345 3412 | Temple Pecan Creek 345 3412
A | Lake Creek 3409 | Temple Switch 3414 | 0.04482 | 0.039033 | 0.038836 | 0.10489 | 0.017691 | 0.021746 | 0.017478 | 0.03186 | 0.021726 | 0.070347 | 0.10043 | 0.11624 | 0.1154 | 0.099321 | 0 | 0.084449 | 0.10563 | 0
| Tradinghouse 3405 | Temple Pecan Creek 3412
B | Lake Creek 3409 | Tradinghouse 3405 | 0.033273 | 0.028847 | 0.028932 | 0.040613 | 0.022884 | 0.023415 | 0.023052 | 0.023421 | -0.028935 | 0.028861 | 0.14098 | 0.17722 | 0.17592 | 0.12861 | 0.31388 | 0 | 0 | 0
| Tradinghouse 3405 | Temple Pecan Creek 3412
C | Temple Pecan Creek 3412 | Temple Switch 3414 | 0.040198 | 0.034971 | 0.03487 | 0.048716 | 0.018289 | 0.039675 | 0.018469 | 0.14194 | 0.039677 | 0.039038 | 0.10771 | 0.12801 | 0.12752 | 0.10649 | 0 | 0.040005 | 0 | 0.17114
| Lake Creek 3409 | Temple Switch 3414
D | Sandow 3429 | Temple 3414 | 0.038259 | 0.033348 | 0.03339 | 0.020744 | 0.011709 | 0.098438 | 0.011393 | 0.060837 | 0.098532 | 0.01653 | 0.063279 | 0.25008 | 0.07124 | 0.12291 | 0.17566 | 0.077641 | 0.14298 | 0.16194
| Sandow 3429 | Temple 3413
E | Sandow 3429 | Austrop 7040 | 0.037536 | 0.032374 | 0.032314 | 0.01848 | 0.081303 | 0.015606 | 0.081009 | 0.035052 | -0.015604 | 0.014477 | 0.020592 | 0 | 0 | 0.067078 | 0.11146 | -0.08534 | 0.082027 | -0.08534
| Sandow 13429 | Austrop 7040
F | Temple | Killeen | 0.030028 | 0.026271 | 0.026257 | 0.026806 | 0.024562 | 0.024097 | 0.023883 | 0.028541 | 0.024134 | 0.019277 | 0.15008 | 0.19099 | 0.18968 | 0.13534 | 0.20403 | 0.079554 | 0.17768 | 0.1836
Notes:
* These values in the cells above are the Zone to Zone Average Weighted Shift Factors for North to South CSC management for the contingency / overloaded elements shown
** For North to South and South to North CSC management, it appears that 345 kV contingencies are the most likely candidates for causing overloads, so we only examined 345 kV contingencies
*** Waco West to Waco Woodway is not currently a CRE for North to South, but prior studies suggested that perhaps it might be a good candidate so we included it here for discussion purposes
**** Temple - Killeen 345 kV is not currently a contingency being considered for North to South CSC management; however, we wanted to take a look at it to see if it might be in some cases

## W-N
West to North CSC
1 |  |  | a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q | r | s | t | u | v | w | x | y
|  | Overloaded Element (Where Green Cell = From Direction) | Long Creek 345 1435 | Murray 138 1371 | Graham SS 138 1601 | Sweetwater 345 1420 | Tonkawa 345 1048 | Flat Creek138 1642 | Jacksboro 345 1429 | Parker 345 1436 | Benbrook 345 1873 | Graham 138 1596 | Parker 345 1436 | Bluff Creek 345 60040 | Jacksboro 345 1429 | Comanche SS 345 1440 | San Angelo Red Creek345 6444 | Graham 345 1430 | Newport 138 1470 | Flat Creek 138 1642 | Long Creek 345 1435 | Paint Creek 138 6169 | Fisher 345 1425 | Barton 138 1599 | Willow Creek 345 1421 | Lingleville 138 1640 | Jacksboro 345 1429
| Contingency |  | Abilene Mulberry 345 6230 | Graham SES 138 1431 | Graham East 1596 | Graham 345 1430 | Graham 345 1430 | Leon 138 1624 | Willow Creek 345 1421 | Graham 345 1430 | Graham 3345 1430 | Barton 138 1599 | Benbrook 345 1869 | Abilene Mulberry 345 6230 | Bowman 345 1422 | Comanche Peak SES 345 1900 | Comanche SS 345 1440 | Jacksboro 345 1429 | Lake Arrowhead 138 1468 | Lingleville 138 1640 | Graham 345 1430 | Murray 138 1371 | Oklaunion 345 6100 | Oran 138 1571 | Parker 345 1436 | Stephanville 138 1641 | West Denton 345 988
A | Graham 1430 | Parker 1436 | 0.10877 | 0.022744 | 0.057069 | 0.1505 | 0.13193 | 0.046002 | 0.32458 | 0 | 0 | 0.06108 | 0.13537 | 0.014041 | 0.14823 | 0.19861 | 0.19826 | 0.37588 | 0.039074 | 0.04565 | 0.12154 | 0.022254 | 0.084736 | 0.06108 | 0.29073 | 0.04565 | 0.19933
| Graham 1430 | Benbrook 1873
B | Bowman 1422 | Fisher 1425 | 0.17715 | 0.028732 | 0.037231 | 0.17951 | 0.15915 | 0.033548 | 0.14888 | 0.19648 | 0.17126 | 0.03842 | 0.079936 | -0.00011515 | 0.065907 | 0.15945 | 0.16329 | 0.19621 | -0.023787 | 0.033236 | 0.19006 | 0.028721 | 0 | 0.040855 | 0.11503 | 0.033241 | 0.11343
| Fisher 1425 | Oklaunion 6100
C | Graham 1430 | Sweetwater 1420 | -0.012903 | 0.043124 | 0.035226 | 0 | 0.25619 | 0.037793 | 0.14096 | 0.15787 | 0.1391 | 0.037357 | 0.071561 | 0.034493 | 0.11749 | 0.21336 | 0.21732 | 0.12884 | 0.026522 | 0.03748 | 0 | 0.043135 | 0.16504 | 0.039792 | 0.10711 | 0.037536 | 0.10586
| Graham 1430 | Long Creek 1435
D | Graham 1430 | Sweetwater 1420 | 0 | 0.042298 | 0.035316 | 0 | 0.25262 | 0.037535 | 0.14158 | 0.15944 | 0.14043 | 0.037383 | 0.072039 | 0.030932 | 0.11634 | 0.21081 | 0.21479 | 0.13107 | 0.026483 | 0.037222 | 0.012903 | 0.042309 | 0.16125 | 0.039818 | 0.10773 | 0.037278 | 0.10633
| Abilene Mulberry 6230 | Long Creek 1435
E | Graham 1430 | Tonkawa 1048 | 0.18904 | 0.028689 | 0.036463 | 0.21424 | 0 | 0.033862 | 0.15159 | 0.15787 | 0.16204 | 0.038243 | 0.079519 | -0.021538 | 0.098363 | 0.16916 | 0.17371 | 0.16729 | 0.025848 | 0.033549 | 0.20195 | 0.028678 | 0.10116 | 0.040678 | 0.11774 | 0.033698 | 0.11389
F | Abilene Mulberry 6230 | Bluff Creek 60040 | 0 | 0.023271 | 0.037014 | 0.16889 | 0.14915 | 0.032319 | 0.15617 | 0.19472 | 0.17101 | 0.038346 | 0.083084 | 0 | 0.09325 | 0.15194 | 0.15612 | 0.18066 | 0.02609 | 0.032006 | 0.15345 | 0.023271 | 0.08241 | 0.040781 | 0.12232 | 0.0319 | 0.11752
G | Bowman 1422 | Jacksboro 1429 | 0.14854 | 0.023194 | 0.039265 | 0.16998 | 0.15008 | 0.034278 | 0.13508 | 0.20754 | 0.17897 | 0.040718 | 0.076388 | -0.009969 | 0 | 0.1542 | 0.15781 | 0.24063 | 0.030388 | 0.033965 | 0.16144 | 0.023189 | 0.069761 | 0.043153 | 0.10122 | 0.033996 | 0.10579
H | Comanche Peak SES 1900 | Comanche SS 1440 | 0.17494 | 0.026843 | 0.039243 | 0.18612 | 0.16565 | 0.030322 | 0.17894 | 0.22248 | 0.19509 | 0.041133 | 0.094251 | -0.05209 | 0.10692 | 0 | 0.06723 | 0.20218 | 0.028349 | 0.03001 | 0.18785 | 0.026747 | 0.098145 | 0.043568 | 0.14509 | 0.030035 | 0.12989
I | Comanche SS 1440 | San Angelo Red Creek 6444 | 0.18509 | 0.028575 | 0.042558 | 0.19272 | 0.17182 | 0.041006 | 0.18285 | 0.22824 | 0.20044 | 0.044194 | 0.098184 | -0.068494 | 0.10903 | 0.033419 | 0 | 0.20741 | 0.029613 | 0.040693 | 0.19799 | 0.028517 | 0.10256 | 0.046629 | 0.149 | 0 | 0.13374
J | Graham 1430 | Jacksboro 1429 | 0.13141 | 0.023021 | 0.04146 | 0.16282 | 0.14366 | 0.035069 | 0.087577 | 0.24721 | 0.20572 | 0.042794 | 0.062053 | -0.0088265 | 0.16879 | 0.15854 | 0.16191 | 0 | 0.026842 | 0.034757 | 0.14431 | 0.023019 | 0.092932 | 0.045228 | 0.053724 | 0.034439 | 0.080983
K | Jacksboro 1429 | Willow Creek 1421 | 0.14006 | 0.023081 | 0.040996 | 0.16612 | 0.14658 | 0.035498 | 0 | 0.24576 | 0.20112 | 0.042737 | 0.047263 | -0.007976 | 0.063976 | 0.15982 | 0.16257 | 0.10692 | 0.030019 | 0.035185 | 0.15296 | 0.023143 | 0.077991 | 0.045172 | -0.033853 | 0.034986 | 0.17054
L | Willow Creek 1421 | Parker 1436 | 0.14077 | 0.023115 | 0.040217 | 0.1666 | 0.14705 | 0.034922 | 0 | 0.23496 | 0.19472 | 0.041891 | 0.055049 | -0.0092286 | 0.070408 | 0.15766 | 0.16067 | 0.12297 | 0.029207 | 0.03461 | 0.15367 | 0.023177 | 0.079176 | 0.044325 | 0 | 0.034411 | 0.15917
M | Jacksboro 1429 | West Denton 988 | 0.14087 | 0.023189 | 0.040569 | 0.16666 | 0.14731 | 0.034354 | 0.21387 | 0.21842 | 0.19011 | 0.042172 | 0.086956 | -0.0099076 | 0.075426 | 0.15563 | 0.15941 | 0.13854 | 0.02968 | 0.034041 | 0.15377 | 0.023143 | 0.080303 | 0.044607 | 0.18002 | 0.034122 | 0
Notes:
* These values in the cells above are the Zone to Zone Average Weighted Shift Factors for West to North CSC management for the contingency / overloaded elements shown
** For West to North and North to West CSC management, it appears that 345 kV contingencies are the most likely candidates for causing overloads, so we only examined 345 kV contingencies

## N-H
North to Houston CSC
5 |  |  | a | b | c | d | e | f | g | h
|  | Overloaded Element (Where Green Cell = From Direction) | Obrien 345 44500 | Jewett 345 3390 | King 345 40900 | King 345 40900 | Roans Prairie 345 40600 | Prairie View 138 7668 | Jewett 345 391 | Kuykendal 345 45971
| Contingency |  | Gibbons Crk 345 967 | THWharton 345 45500 | Kuykendal 345 45971 | Kuykendal 345 45972 | Kuykendal 345 45972 | Waller 138 7272 | Tomball 345 6500 | Tomball 345 6500
A | THWharton 45500 | Jewett 3390 | 0.26143 | 0 | 0.0089214 | 0.28349 | -0.0082809 | 0.026624 | 0 | 0.0087762
| Tomball 46500 | Jewett 3391
B | THWharton 45500 | Jewett 3390 | 0 | 0 | 0.16436 | 0.29893 | 0.29899 | 0.017819 | 0.26889 | 0.1644
| Gibb Crk 967 | Obrien 44500
C | Kuykendal 45972 | Roans Prairie 40600 | 0.30561 | 0.27319 | 0.029586 | 0 | 0 | 0.025813 | 0 | 0.029596
| Tomball 46500 | Jewett 3391
D | Kuykendal 40900 | King 45972 | 0.24769 | 0.22277 | 0 | 0 | 0 | 0.011087 | 0.17141 | 0
| Kuykendal 40900 | King 45971
Notes:
* These values in the cells above are the Zone to Zone Average Weighted Shift Factors for North to Houston CSC management for the contingency / overloaded elements shown
** For North to Houston CSC management, it appears that 345 kV contingencies are the most likely candidates for causing overloads, so we only examined 345 kV contingencies