ERCOT Protocols

Section 10:  Metering

May 1, 2008

10	Metering	10-1

10.1	Overview	10-1

10.2	Scope of Metering Responsibilities	10-1

10.3	Meter Data Acquisition System (MDAS)	10-3

10.4	Certification of ERCOT Polled Settlement Metering Facilities	10-10

10.5	TDSP ERCOT Polled Settlement Meter Inspectors	10-13

10.6	Auditing and Testing of Metering Facilities	10-15

10.7	ERCOT Request for Installation of ERCOT Polled Settlement Metering Facilities	10-16

10.8	Maintenance of Metering Facilities	10-17

10.9	Standards for Metering Facilities	10-18

10.10	Security of Meter Data	10-20

10.11	Validating, Editing, and Estimating of Meter Data	10-22

10.12	Communications	10-23

10.13	Meter Identification	10-23

10.14	Exemptions from Compliance to Metering Protocols	10-24

# Metering

10.1	Overview

This Section specifies the responsibilities and requirements for meter data, certification of Metering Facilities, meter standards, approved meter types and the process for auditing, testing, and maintenance of Metering Facilities to be used in the ERCOT Region.

Transmission and/or Distribution Service Providers (TDSP) are the only Entities authorized to provide Settlement Meter data to ERCOT.  ERCOT shall maintain a Meter Data Acquisition System (MDAS) to collect generation and consumption energy data for settlement purposes under these Protocols.  The MDAS must receive Customer Load meter data from TDSPs and must collect data from all ERCOT-Polled Settlement (EPS) Meters.

All Service Delivery Points (SDPs), excluding EPS, generation, or Non Opt-In Entity (NOIE) metering points, that meet the requirements of PUCT Substantive Rule 25.311 are eligible for competitive meter ownership pursuant to such PUCT Substantive Rule.  All competitively owned meters shall meet all the applicable metering requirements of the ERCOT Protocols and Competitive Metering Guides.

10.2	Scope of Metering Responsibilities

10.2.1	QSE Real-Time Metering

The QSE’s responsibility for Real-Time metering requirements for Ancillary Service verification is contained in Section 6.5.1.1, General Technical Requirements.

10.2.2	TDSP Metered Entities

TDSPs are responsible for supplying ERCOT with meter data associated with:

(1)	All Loads using the ERCOT System;

(2)	Any Generation Resource that delivers less than ten (10) MW to the ERCOT System and that is connected directly to the distribution system; a TDSP may make some or all such meters ERCOT-Polled Settlement (EPS) compliant and may request that ERCOT poll the meters. Notwithstanding the foregoing sentence, meter data is not required from:

(a)	generation owned by a NOIE and used for NOIE’s self-use (not serving Customer Load); and

(b)	renewable generation with a design capacity less than fifty (50) kW interconnected to a TDSP and not registered as a Generation Resource; and

(3)	NOIE points of delivery where metering points are radial Loads and are unidirectionally metered.  The TDSPs have the option of making some or all such meters EPS compliant and to request that ERCOT poll the meters.

Each TDSP is responsible for the following:

(1)	Compliance with the procedures and standards in this Section, the Settlement Metering Operating Guides (SMOG) and the Operating Guides;

(2)	Installation, control, and maintenance of the settlement Metering Facilities, as more fully described in this Section and the SMOG, which includes meters, recorders, instrument transformers, wiring, and miscellaneous equipment required to measure electrical energy;

(3)	Costs incurred in the installation and maintenance of these Metering Facilities and communications except for incremental costs incurred for functions not required for the settlement of the Load or Resource.  These incremental costs shall be borne by the Entities requesting the service pursuant to the TDSP’s tariffs; and

(4)	Installation, maintenance, data collection, and related communications, telemetry for the Metering Facilities, and related services necessary to meet the mandatory IDR requirements detailed in this Section, Section 18 Load Profiling, and the SMOG.

10.2.3	ERCOT Polled Settlement Meters

ERCOT shall poll Metering Facilities that meet any one of the following criteria:

(1)	Generation connected directly to the ERCOT Transmission Grid;

(2)	Auxiliary meters used for generation netting by ERCOT;

(3)	Generation delivering ten (10) MW or more to the ERCOT System;

(4)	Generation participating in any Ancillary Service market;

(5)	NOIE points connected bi-directionally to the ERCOT system; and

(6)	Direct Current Ties.

Additionally, ERCOT shall poll any generator or NOIE metering point at the request of such Entity, provided the Metering Facility meets all requirements and approvals associated with EPS metering requirements of this Section and the SMOG.  Loads acting as a Resource of ten (10) MW or more on the ERCOT System may, at their option, have an EPS meter.

10.2.3.1	Entity ERCOT Polled Settlement Responsibilities

The following defines the responsibilities of Entities regarding EPS metering:

(1)	EPS Meters must be polled directly by ERCOT, which shall then convert the raw data to Settlement Quality Meter Data in accordance with this Section, Section 11, Data Acquisition and Aggregation, and the SMOG;

(2)	TDSPs shall have EPS Metering Facilities installed and maintained under the supervision of a TDSP “EPS Meter Inspector,” which is defined as an employee or agent of the TDSP who has received EPS training from ERCOT, and is described further herein;

(3)	TDSPs shall install, control, and maintain the meters, recorders, instrument transformers, wiring, communications, and other miscellaneous equipment required to measure electrical energy, as described in this Section and the SMOG;

(4)	TDSPs shall install and maintain “Back-up Meters” at each EPS Meter location for Resources, auxiliary netting, and bi-directional meter points.  A Back-up Meter is defined as a redundant revenue quality EPS Meter connected at the same metering point as the primary EPS Meter and meeting the requirements defined in the SMOG;

(5)	Costs incurred in the installation and maintenance of EPS metered Facilities and communications will be the responsibility of the TDSP except for incremental costs incurred for functions not required for the energy settlement as required by these Protocols.  These incremental costs shall be borne by the Entities requesting the service, as per the TDSP’s tariffs; and

(6)	Specific operating practices for EPS Metering Facilities are included in the SMOG.

10.3	Meter Data Acquisition System (MDAS)

10.3.1	Purpose

The MDAS will be used:

(1)	By ERCOT to obtain and receive Revenue Quality Meter data from the EPS Meters and Settlement Quality Meter Data from the TDSP for settlement and billing purposes; and

(2)	To populate the ERCOT Data Archive used by Market Participants or their agents with authority to access Settlement Quality Meter Data held by ERCOT.

10.3.2	ERCOT-Polled Settlement Meters

Each TDSP shall, in accordance with these Protocols and the SMOG, provide ERCOT approved metering communication equipment and connection to permit ERCOT access to the TDSP’s EPS Meters.

ERCOT shall retrieve meter data electronically and automatically by MDAS.  ERCOT may also collect meter data on demand.

10.3.2.1	Generation Meter Splitting

Each Generation Resource meter must be represented by only one QSE, except that a jointly owned Generation Resource unit or group of Generation Resources may split the net generation output into two or more virtual generating units for a Generation Entity.  Each Generation Entity representing a virtual generating unit may have its energy and capacity scheduled through separate QSEs.  For purposes of this paragraph, a jointly owned Generation Resource unit or group of Generation Resources shall also include the San Miguel and Gibbons Creek power projects, and intermittent Resources such as wind and solar generation.

When the Generation Resource unit is registered with ERCOT, the Entities representing virtual generator units shall be required to submit a percentage allocation of the Resource to be used to determine the capacity available at each virtual generator unit.

When the generator unit is registered with ERCOT, the owners of the unit shall submit all required ERCOT Facility registration documentation and an ERCOT-approved splitting agreement executed by an authorized representative from each owning Entity.  Such agreement shall contain a defined and fixed ownership percentage as among the owning Entities.  ERCOT shall establish this generator as a “split,” essentially establishing a virtual generator meter.  Generation splitting based on a static ratio is not permitted.  Generation splitting requires Real-Time splitting signals.

10.3.2.1.1	Generator Metering Real-Time Splitting Signal

When the split-metered generating unit is registered at ERCOT, the Entities representing the virtual generator units shall select one master QSE to provide ERCOT with a Real-Time signal of the MW of generation per virtual generator unit.  The signal must be sent from the master QSE’s EMS system to ERCOT via the appropriate telemetry.  The signal must be revised every scan cycle and must represent each virtual generator unit in positive MW.  The signal must contain the Resource ID (RID) and the MW assigned to that RID.

ERCOT shall integrate the signals and provide a MWh value for each 15-minute interval for each virtual generator unit.  The settlement system must use the MWh per interval value to calculate the percentage breakdowns to be applied to the actual metered MWh values retrieved from the EPS metered Entity.

10.3.2.1.2	Allocating ERCOT Polled Settlement Metered Data to Generator Virtual Meters

ERCOT shall poll the EPS Metering Facilities related to the actual Generation Resource and store the meter data at 15-minute intervals.  This metering data must be validated, edited, estimated, and compensated for losses, as necessary, and be netted as required.  This resulting data must then have the virtual generator ratios applied to assign the generation to the QSE representing each owner of the virtual generators.  The MWh quantities of the virtual generators must be used in all settlement calculations and reports.

The following example illustrates the splitting of the generation data:

Splitting Example 1

| Integrated values from ERCOT systems |  |  |  |  |  |  | Actual Metered MWh | Data to be Used in Settlement |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Interval Ending | RID1 (MWh) | RID2 (MWh) | RID3 (MWh) | Total MWh |  | % Ratios Rid 1,2,3 |  | Split MWh | Split MWh | Split MWh |
| 13:15 | 10 | 20 | 10 | 40 |  | 25, 50, 25 | 52 | 13 | 26 | 13 |

10.3.2.1.3	Processing for Missing Dynamic Splitting Signal

For any interval when ERCOT has not received a Real-Time signal for any one of the virtual generating units, ERCOT shall use the last valid percentage ratio for a completed interval.

Splitting Example 2

| Integrated values from ERCOT systems |  |  |  |  |  |  | Actual Metered MWh | Data to be Used in Settlement |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Interval Ending | RID1 (MWh) | RID2 (MWh) | RID3 (MWh) | Total MWh |  | % Ratios Rid 1,2,3 |  | Split MWh | Split MWh | Split MWh |
| 13:15 | 10 | 20 | 10 | 40 |  | 25, 50, 25 | 52 | 13 | 26 | 13 |
| 13:30 | NA | 21 | 10 | NA |  | Ratio Above | 55 | 13.75 | 27.5 | 13.75 |
| 13:45 | NA | 22 | 10 | NA |  | Ratio Above | 48 | 12 | 24 | 12 |

10.3.2.1.4	Calculating the Virtual Generator Ratio

For split-metered generating units, ERCOT shall provide for settlement the net MWh value for each 15-minute interval.  This value is the MWh accumulated based on the MW value over each scan cycle.  ERCOT shall use a standard “integration” mechanism to perform this function.

For settlement, ERCOT shall use the integrated data to determine the allocation ratio as the integrated share of each signal divided by the integrated total of signals.

10.3.2.1.5	Generation Splitting Data made available to Market Participants

Market participants shall have access to allocated generation output and ratio data only for virtual generators that they represent.  ERCOT shall provide the allocation ratio for that RID.  The master QSE for a split-metered generator unit shall have access to the allocation ratios and assigned generation output for units in which they act as the master QSE.

10.3.2.1.6	Allocating ERCOT Polled Settlement Metered Data to Generator Owners When it is Net Load

EPS Generation Resource sites that are netted by ERCOT may have multiple CRs associated with the Load.  ERCOT shall poll the EPS metering Facilities related to the actual Generation Resource Facility and store the meter data at 15-minute intervals.  ERCOT shall perform validation, editing, estimation, compensation for losses as necessary, and netting as required for EPS metering data.  For intervals when data is net Load, the fixed ownership percentages stored in the asset database must be used to allocate the consumption to multiple ESI IDs.  The consumption quantities for the ESI IDs must be used in all energy settlement calculations and reports.

10.3.2.2	Loss Compensation of ERCOT Polled Settlement Meter Data

Where the EPS Meter is not located at the point of interconnection to the ERCOT Transmission Grid, actual metered consumption must be adjusted for line and transformation losses to the point of interconnection.  The preferred method for loss compensation and correction is via internal meter programming.

Recognizing the fact that some locations may not have the total functionality necessary to perform internal compensation, the MDAS must have the functionality to perform approved loss compensation as necessary.  ERCOT shall retain the discretion to allow or deny the continued use of this type of metering.

No meter may be compensated internally for losses more than once.  ERCOT may compensate multiple meters prior to netting to the point of interconnection.  Pulse communications transfer of data between meters is not allowed.

10.3.2.3	Generation Netting for ERCOT Polled Settlement Meters

At Generation Resource Facilities, generation and associated Loads, including construction and maintenance Load that is netted with existing generation auxiliaries, must be metered at their points of interconnection to the ERCOT Transmission Grid.  Interval Data Recorder (IDR) meters must be used to determine generator output or Load usage.  In the intervals where the generation output exceeds the Load, the net must be settled as generation.  In the intervals where the Load exceeds the generation output, the net must be settled as Load and carry any applicable Load shared charges.

For settlement purposes, generation netting is not allowed except under one of the following conditions:

(1)	Single point of interconnection with delivered and received metering data channels;

(2)	Multiple points of interconnection where the Loads and generator output are electrically connected to a common switchyard, as defined below.  In addition, there must be sufficient generator capacity to serve all plant Loads for netting to occur;

(3)	A Qualifying Facility (QF) with point(s) of interconnection where the QF is selling to the QF’s thermal host(s) may net the Load meters of the thermal host with its generation meters when the Load and generation are electrically connected to a common switchyard.  In instances in which Load is served by new on-site generation through a common switchyard, the TDSPs may install monitoring equipment necessary for measuring Load to determine stranded cost charges, if any are applicable, as determined under PURA and applicable PUCT rules.  If the PUCT requires other Load served by onsite generators to pay the System Benefit Fund charges, then, in instances in which Load is served by generation through a common switchyard, the TDSP may install metering equipment solely for purposes of the TDSP’s calculation of System Benefit Fund charges, as provided by PURA, if any is applicable.  For purposes of this Section, new on-site generation has the meaning as contained in PURA Sections 39.252 and 39.292(k); or

(4)	For Generation Resources and/or Load with flow-through on a private, contiguous transmission system (not included in a TDSP rate base) and in a configuration existing as of October 1, 2000, the meters at the interconnections with the ERCOT Transmission Grid may be netted for the purpose of determining Generation Resources or Load.  For Settlement purposes, the metered interconnection points must be assigned to the same Congestion Zone and UFE Zone.

For purposes of this Section, a common switchyard is defined as an electric substation Facility where the point of interconnection for Load and Generation Resources are located at the same Facility but where the interconnection points are physically not greater than 400 yards apart.  The physical connections of the Load to its point of interconnection and the Generation Resource to its point of interconnection cannot be Facilities that have been placed in a TDSPs rate base.

10.3.2.4	Reporting of Net Generation Capacity

All Generation Resource Facilities with associated Load shall report to ERCOT before February 1st of each year their projected Net Generation capacity available to the grid for use by others during the June to August time period for the current calendar year and five (5) subsequent years in the same format as the generation capacity reports provided to the PUC.

10.3.3	TDSP Metered Entities

10.3.3.1	Data Responsibilities

TDSPs shall be responsible for the following:

(1)	Providing consumption data for each ESI ID and RID on a monthly basis according to the data timeliness and accuracy standards defined in this Section and in the SMOG;

(2)	Providing start date, stop date, ESI ID or RID, and consumption data in kWh as well as an identifier for “estimated” reads as applicable;

(3)	Submitting a single demand value for each non-IDR ESI ID that has a demand register to ERCOT if, and only if, a demand value is required for TDSP tariffs or for CR customer billing.  If the CR and TDSP do not require a demand value, then the TDSP shall not submit a demand value to ERCOT even if the meter has a demand register;

(4)	Validating, Editing, and Estimating (VEE) meter data according to the standards in this Section before submitting data to the settlement process;

(5)	Calculating consumption for any unmetered services by ESI ID and submitting such data monthly to ERCOT, subject to ERCOT audit.  These calculations must be made pursuant to TDSPapproved tariffs; and

(6)	Metering all Loads, unless the Load meets the following criteria:

(a)	Energy consumption by substation Facilities and equipment for the purpose of transporting electricity (e.g., substation transformers, fans, etc.).

(b)	Unmetered energy consumption represented by an ERCOT-approved Load Profile.

10.3.3.2	Retail Load Meter Splitting

Retail Service Delivery Points with Loads above one (1) MW may split their actual meter data into a maximum of four consumption values with each value being assigned a unique ESI ID; provided, however, that if a Customer is using Provider of Last Resort (POLR) or the “Price-to-Beat” retail service, such Customer may not split its meter signal among multiple CRs through this Section.

10.3.3.2.1	Retail Customer Load Splitting Mechanism

Customer meter data may be split into separate ESI IDs by the installation of a programmable signal splitter that would take the master meter signal and split it into no more than four (4) separate values that must at all times equal the total output of the master meter signal.  Splitting of Customer meter data must meet the following requirements:

(1)	The signal splitter may be programmed to split the Load in any way the Customer chooses, provided that such splitting results in positive Load;

(2)	The Customer, or its CR(s), shall provide the signal splitter and shall be responsible for all costs of installing, maintaining, and operating the signal splitter, any associated equipment, and communications;

(3)	The TDSP shall be responsible for approving the specifications and installation of any signal splitting devices;

(4)	Interval Data Recorders shall be required on the master Customer Load meter and each of the split channels for verification and settlement purposes;

(5)	The TDSP metering system recording such split signals (four (4) ESI IDs) may be required to be redundant if so provided by TDSP tariffs;

(6)	The split signals must be recorded in Real-Time and cannot be altered or substituted later in time;

(7)	One Entity shall be designated to pay the total TDSP charges for the Customer; and

(8)	Switching of CRs for the individual split-metered Customers shall comply with the registration procedures in Section 19, Texas Standard Electronic Transaction (SET).

10.3.3.2.2	TDSP Responsibilities Associated With Retail Customer Load Splitting

(1)	Each consumption value from a Customer Load split meter shall be assigned a separate ESI ID by the TDSP.  Each ESI ID may be assigned to a separate CR.  The master meter may not be assigned an ESI ID.

(2)	The TDSP shall send interval data for each ESI ID for the ERCOT settlement system.

(3)	The TDSP shall be responsible for verifying that the sum of the split ESI ID IDR data equals the total IDR value from the master meter.

10.3.3.2.3	ERCOT Requirements for Retail Load Splitting

(1)	ERCOT shall settle all ESI IDs in the same manner.

(2)	ERCOT shall not receive or process the IDR data associated with the master meter.

10.3.3.3	Method for Interfacing with MDAS

Settlement Meter data shall be submitted to ERCOT on a periodic cycle, but no later than monthly, using the Texas SET meter data exchange format.  Each TDSP shall ensure that consumption meter data submitted to ERCOT is in intervals of:

(1)	15-minutes for those ESI IDs and RIDs served by IDRs; and

(2)	Monthly or on an ERCOT-approved meter reading cycle for non-IDR meters.

The Settlement Quality Meter Data submitted by TDSPs must be in kWh and kVarh values (as applicable).

10.3.3.3.1	Past Due Data Submission

ERCOT shall provide a report to the appropriate TDSP for any ESI ID or RID for which consumption data has not been received in the past thirty-eight (38) days.  Upon receipt of the missing consumption data report, the TDSP shall have two (2) Business Days to submit the missing consumption data.

10.4	Certification of ERCOT Polled Settlement Metering Facilities

Each TDSP shall certify EPS Metering Facilities in a manner approved by ERCOT.

10.4.1	Overview

This Section describes the steps that TDSPs shall use to certify each EPS Metering Facility and the steps ERCOT shall use to approve each EPS Metering Facility.  This Section also describes the manner in which EPS Metering Facility approval requests must be made to ERCOT.

10.4.2	ERCOT Polled Settlement Design Proposal Documentation Required From the TDSP

Before installation of new EPS Meters, the TDSP shall provide ERCOT with an EPS Design Proposal of the Metering Facilities being considered for ERCOT approval as EPS Meter Facilities.  An “EPS Design Proposal” is the documentation required on the form available on the MIS. Included one line drawings must be dated, detailed, bear the current drawing revision number, and show all devices which contribute to the burden in the metering circuits.  Other information may also be required by ERCOT for review regarding the meter and related installation and Facilities; such additional information shall be promptly provided to ERCOT by the TDSP upon ERCOT’s request.

10.4.2.1	Approval or Rejection of an ERCOT Polled Settlement Design Proposal for ERCOT Polled Settlement Metering Facilities

ERCOT may unconditionally approve, conditionally approve, or reject an EPS Design Proposal.

10.4.2.1.1	Unconditional Approval

If ERCOT unconditionally approves an EPS Design Proposal, then ERCOT shall promptly notify the TDSP that the EPS Design Proposal has been approved.  The TDSP may then commence installation of the EPS Metering Facilities in accordance with the EPS Design Proposal.

10.4.2.1.2	Conditional Approval

(1)	Notification of Conditional Approval:

If ERCOT conditionally approves an EPS Design Proposal, then ERCOT shall promptly notify the TDSP that the EPS Design Proposal has been conditionally approved.  It shall set forth in such Notice the conditions on which approval is granted and the time period in which each such condition must be satisfied by the TDSP.

(2)	Ability to Satisfy Conditions:

If the TDSP disputes any condition imposed by ERCOT, the TDSP must promptly notify ERCOT of its concerns and provide ERCOT with the reasons for its concerns.  If the TDSP provides ERCOT such Notice, ERCOT may amend or withdraw any of the conditions on which it granted its approval or ERCOT may require the TDSP to satisfy other conditions.  ERCOT and the TDSP shall use good faith efforts to reach agreement on accomplishing the installation.

(3)	Notification of Satisfaction of Conditions:

The TDSP shall promptly notify ERCOT when each condition in the approval has been satisfied and provide to ERCOT any information reasonably requested by ERCOT as evidence that such condition has been satisfied.

(4)	Confirmation of Satisfaction of Conditions:

If ERCOT determines that a condition has been satisfied, then ERCOT shall provide the TDSP written confirmation that the condition has been satisfied.

(5)	Unsatisfied Conditions:

If ERCOT determines that a condition has not been satisfied, ERCOT shall notify the TDSP that it does not consider the condition satisfied and shall set out in such Notice the reason(s) that it does not consider the condition satisfied.  If, after using good faith efforts, ERCOT and the TDSP are unable to agree on whether the condition is satisfied, either Entity may refer the dispute to the Alternative Dispute Resolution (ADR) Procedures as described in Section 20, Alternative Dispute Resolution Procedure.

10.4.2.1.3	Rejection

If ERCOT rejects an EPS Design Proposal, then ERCOT shall promptly notify the TDSP that the EPS Design Proposal has been rejected and shall set forth the reasons for its rejection.  The TDSP shall submit to ERCOT a revised EPS Design Proposal after receiving such Notice.  If ERCOT rejects for a second time an EPS Design Proposal submitted by a TDSP with respect to the same or similar Notice issued by ERCOT as described above, then ERCOT and the TDSP shall use good faith efforts to reach agreement on the requirements and disputed items.  In the absence of agreement either entity may refer the dispute to the ADR Procedures as described in Section 20, Alternative Dispute Resolution Procedure.

10.4.3	Site Certification Documentation Required from the TDSP ERCOT Polled Settlement Meter Inspector

A TDSP EPS Meter Inspector shall complete an ERCOT site certification form for each set of EPS Metering Facilities that it inspects.  The site certification form is the official form used to document whether EPS Metering Facilities meet ERCOT criteria.

The TDSP EPS Meter Inspector shall promptly notify ERCOT and document any discrepancy between ERCOT approved EPS Design Proposal on file and the actual Metering Facilities inspected by the TDSP EPS Meter Inspector.

The TDSP shall provide the documents as outlined in SMOG for each set of EPS Metering Facilities being considered for ERCOT approval.

10.4.3.1	Review by ERCOT

ERCOT shall review the ERCOT site certification documentation prepared by the TDSP EPS Meter Inspector within forty-five (45) days of receipt.  If ERCOT finds that this data is incomplete or demonstrates that the EPS Metering Facilities fail to meet the standards contained within this Section or the SMOG, ERCOT shall promptly provide written or electronic notice of the deficiencies to the TDSP.

ERCOT shall notify the TDSP of the approval of the Metering Facility.  ERCOT shall return the original schematic drawings, and the original ERCOT site certification form stamped by ERCOT as approved.  ERCOT shall retain a copy of the documents.

10.4.3.2	Provisional Approval

If ERCOT finds that the documentation: provided by the TDSP is incomplete or demonstrates that the EPS Metering Facility fails to meet the standards contained within this Section and the SMOG; then ERCOT may elect to issue a provisional approval for the Metering Facility.  The terms and conditions on which such provisional approval is issued shall be at ERCOT’s discretion and shall be defined for the TDSP.  ERCOT shall not issue an approval until such time as all of the conditions of the provisional approval have been fulfilled to the satisfaction of ERCOT.  ERCOT shall post any provisional approvals on the MIS on a quarterly basis.

10.4.3.3	Obligation to Maintain Approval

Once an EPS Metering Facility has been installed, it is the responsibility of the TDSP to ensure that the EPS Metering Facility complies with the approval criteria referred to in this Section and the SMOG.

10.4.3.4	Revocation of Approval

ERCOT may revoke in full or in part any approval of Metering Facilities, including a provisional approval if:

(1)	ERCOT or a TDSP EPS Meter Inspector demonstrates that all or part of the EPS Metering Facilities covered by that approval no longer meet the approval criteria for EPS Metering Facilities contained in this Section and the SMOG; and

(2)	ERCOT has given written Notice to the TDSP stating that the identified EPS Metering Facilities do not meet the approval criteria and the reasons and that the TDSP fails to correct the deficiency and satisfy ERCOT, within thirty (30) days, that the EPS Metering Facilities meet the approval criteria.

If ERCOT revokes in full or part an approval of EPS Metering Facilities, the TDSP may seek re-approval of the EPS Metering Facilities by requesting approval in accordance with this Section.

10.4.3.5	Changes to Approved ERCOT Polled Settlement Metering Facilities

Each TDSP shall notify ERCOT of any planned modifications or changes to be made to any EPS Metering Facilities that would affect the EPS Metering Facility’s approval, not less than ten (10) Business Days prior to the intended implementation of the change.  Before the intended date of the change, ERCOT may request additional information from the TDSP to demonstrate that the EPS Metering Facilities will still meet the applicable approval standards; the TDSP shall promptly comply with such request for information.  ERCOT may at its discretion audit Metering Facilities to determine compliance.  The TDSP shall provide ERCOT with meter specific program details, as downloaded from the meter, when the EPS Meter is programmed.

10.4.3.6	Confirmation of Certification

On the written request of ERCOT, the TDSP shall provide ERCOT written or electronic confirmation that the Metering Facilities of each metered Entity that the TDSP represents have been certified in accordance with this Section and the SMOG within five (5) Business Days of receiving such a request from ERCOT.

10.5	TDSP ERCOT Polled Settlement Meter Inspectors

10.5.1	List of TDSP ERCOT Polled Settlement Meter Inspectors

ERCOT shall maintain a list of TDSP EPS Meter Inspectors, and details related to ERCOT training to become a TDSP EPS Meter Inspector.

10.5.2	ERCOT Polled Settlement Meter Inspector Approval Process

10.5.2.1	TDSP Responsibilities

Each TDSP shall ensure that personnel performing EPS Meter Facility certification duties are approved EPS Meter Inspectors and comply with this Section and the SMOG.  A TDSP EPS Meter Inspector is required to complete an ERCOT EPS Meter Inspector training session.

The TDSP shall submit to ERCOT the following information for individuals performing EPS Metering Facility certification:

(1)	Name of individual;

(2)	Time period the individual has been testing Generation Resource or transmission interconnect metering points;

(3)	TDSP statement indicating that the individual has the technical expertise to perform EPS Metering Facility certification; and

(4)	Additional documentation as required by ERCOT.

10.5.2.2	ERCOT Responsibilities

ERCOT shall hold EPS Meter Inspector training sessions on a regularly scheduled basis.  Sessions must include information on the following:

(1)	Market responsibilities of EPS Meter Inspectors;

(2)	Documentation requirements for the site certification;

(3)	Overview of EPS Metering Facilities related topics and documents;

(4)	Protocols requirements;

(5)	SMOG requirements; and

(6)	Technical requirements.

ERCOT shall issue a certificate of attendance to individuals upon completion of the EPS Meter Inspector training sessions.

ERCOT shall have the authority to revoke an individual’s involvement with EPS Metering Facility certification.

10.6	Auditing and Testing of Metering Facilities

10.6.1	ERCOT Polled Settlement Meter Entities

10.6.1.1	ERCOT Requirement for Audits and Tests

ERCOT shall have the right to audit any EPS Metering Facility that it considers necessary or to request and witness a test carried out by a TDSP EPS Meter Inspector.

10.6.1.2	TDSP Testing Requirements for ERCOT Polled Settlement Metering Facilities

At a minimum, the TDSP EPS Meter Inspector shall conduct testing of EPS Meters on an annual basis, within the same month of each year as the previous year’s test.  Metering Facilities used in the ERCOT system for settlement must be tested pursuant to the TDSP tariffs, the SMOG and these Protocols.

Instrument transformers used in settlement metering circuits must be tested using the following guidelines:

(1)	Magnetic Instrument Transformers do not require periodic testing as they have shown themselves to be stable per ANSI C12.1.;

(2)	Coupling Capacitor Voltage Transformers (CCVTs) shall, at a minimum, be tested for accuracy on a five (5) year cycle, by the end of the fifth year after the previous test; and

(3)	Fiber-optic Current Transformers (CTs) shall, at a minimum, be ratio tested on a five (5) year cycle, by the end of the fifth year after the previous test.

ERCOT may determine that periodic testing of CCVTs and fiber-optic CTs is not required once these devices have been proven to be stable.  If the devices have shown themselves to be unstable, ERCOT may discontinue the use of these devices for settlement purposes.

10.6.1.3	Failure to Comply

If an EPS Metering Facility fails to comply with ERCOT’s audit or test procedures, ERCOT shall issue a warning to the TDSP responsible for such Metering Facilities.  If the TDSP fails to comply with ERCOT’s recommendations in a reasonable time, as determined by ERCOT, ERCOT shall notify the PUCT or the appropriate Governmental Authority.

10.6.1.4	Requests by Market Participants

Market Participants shall follow appropriate Governmental Authority rules for requesting the testing of Metering Facilities.

10.6.2	TDSP Metered Entities

10.6.2.1	Requirement for Audit and Testing

(1)	Audit and Testing by TDSP

Each TDSP shall conduct (or engage a qualified Entity to conduct) audits and tests of the Metering Facilities of the TDSP Metered Entities that it represents to ensure compliance with all applicable requirements of any relevant Governmental Authority.  Each TDSP shall undertake any other actions that are reasonably necessary to ensure the accuracy and integrity of the meter data.

(2)	Audit and Testing Requests by an affected Market Participant

Subject to any applicable Governmental Authority requirements, an affected Market Participant shall have the right to witness an audit or test carried out by the TDSP or its authorized representative.

10.6.2.2	TDSP Requirement to Certify per Governmental Authorities

If a Governmental Authority has authority to certify meter installations, then the TDSPs shall comply with such regulations.

10.7	ERCOT Request for Installation of ERCOT Polled Settlement Metering Facilities

10.7.1	Additional ERCOT Polled Settlement Metering Installations

If ERCOT determines that there is a potential need to install additional EPS Metering Facilities on the ERCOT System, ERCOT shall notify the relevant TDSP in writing or electronically.  ERCOT’s Notice must include the following information:

(1)	The location of the meter point at which the additional EPS Metering Facilities are required;

(2)	The projected installation date by which the relevant EPS Metering Facilities should be installed;

(3)	The reason for the need to install the additional EPS Metering Facilities; and

(4)	Any other information that ERCOT considers relevant.

A TDSP that is notified by ERCOT of the potential need to install additional EPS Metering Facilities must:

(1)	Give ERCOT written confirmation of receipt of Notice within three (3) Business Days of receiving such Notice;

(2)	Submit an EPS Design Proposal to ERCOT within forty-five (45) Business Days of receiving such Notice.

The TDSP may request a waiver to install additional Metering Facilities.

10.7.2	Approval or Rejection of Waiver Request for Installation of EPS Metering Facilities

ERCOT may approve or reject a waiver request at ERCOT’s sole discretion.

10.7.2.1	Approval

If ERCOT approves a waiver request, then ERCOT shall promptly notify the TDSP.

10.7.2.2	Rejection

If ERCOT rejects a waiver request, then ERCOT shall promptly notify the TDSP and shall set forth the reasons for its rejection.  The TDSP may submit to ERCOT a revised waiver request within fourteen (14) Business Days of receiving such Notice.  If ERCOT rejects, for a second time, a waiver request submitted by a TDSP with respect to the same or similar Notice issued by ERCOT as described above, then ERCOT and the TDSP shall use good faith efforts to reach agreement on the requirements and disputed items.  In the absence of agreement either entity may refer the dispute to the ADR Procedures as described in Section 20, Alternative Dispute Resolution Procedures.

10.8	Maintenance of Metering Facilities

10.8.1	ERCOT Polled Settlement Meters

10.8.1.1	Duty to Maintain ERCOT Polled Settlement Metering Facilities

Each TDSP shall maintain its EPS Metering Facilities to meet the standards prescribed by this Section and the SMOG.  If the EPS Metering Facilities of a TDSP require maintenance to ensure that they operate in accordance with the requirements of this Section, the SMOG, or any Governmental Authority, then the TDSP shall notify ERCOT of the need for such maintenance.  The TDSP shall also inform ERCOT five (5) Business Days in advance of the time period during which such maintenance is expected to occur.  During that period, the TDSP, or its authorized representative, after notifying ERCOT, shall be entitled to access sealed EPS Metering Facilities to which access is required in order to undertake the required maintenance.

10.8.1.2	ERCOT Polled Settlement Metering Facilities Repairs

If an EPS Metering Facility requires repairs to ensure that it operates in accordance with the requirements of this Section, then the TDSP shall immediately notify ERCOT of the need for repairing such Facility.  If, however, operating conditions are such that it is not possible for the TDSP to notify ERCOT of the need for repairs, then the TDSP may make the necessary repairs and then notify ERCOT of the repairs prior to the end of the next Business Day.

(1)	Where no Back-up Meter exists or back-up meter data is unavailable, the TDSP shall ensure that the metering point is repaired and operational within twelve (12) hours of problem detection;

(2)	Where a functional and operational Back-up Meter exists, the TDSP shall ensure that the metering point is repaired and operational within five (5) Business Days of problem detection.

10.8.2	TDSP Metered Entities

Each TDSP shall maintain its Metering Facilities in accordance with the requirements of the relevant Governmental Authorities and according to this Section.

10.9	Standards for Metering Facilities

For settlement purposes, IDR meters are required on any of the following locations/sites:

(1)	Generation Resources (with the exception of those excluded in this Section);

(2)	Resources bidding into the Ancillary Services Market;

(3)	NOIE metering points used to determine NOIE total Load;

(4)	Service Delivery Points connected to the transmission system (>60KV); and

(5)	Locations meeting IDR Requirements defined in Section 18, Load Profiling.

10.9.1	ERCOT-Polled Settlement Meters

The TDSP for EPS meters shall ensure that the EPS Metering Facilities comply with this Section and the SMOG.

IDR meters used for settlement of EPS Metering Facilities shall:

(1)	Capture energy consumption and/or production in increments consistent with ERCOT defined Settlement Interval;

(2)	Be able to capture energy in increments of five (5) minutes (excluding memory allocation) for new and replacement IDR meters used for settlement;

(3)	Provide interval data for daily polling on a schedule that supports ERCOT’s requirements (typically a daily cycle);

(4)	Be capable of having data retrieved via telemetry by MDAS;

(5)	Have battery or other energy-storage back-up to maintain time during power outages;

(6)	Have remote time synchronization capability compatible with the MDAS;

(7)	Maintain meter clocks on a time reference standard that enables ERCOT MDAS to maintain the IDR data on the Central Prevailing Time.  The meter clock shall be synchronized to within +/- one percent (1%) of the Settlement Interval when compared with the National Institute of Standards and Technology (NIST) Atomic Clock.  ERCOT shall perform the time synchronization for meters at the time of the interrogation if the meter is outside tolerance; and

(8)	Divide each hour into Settlement Intervals ending as follows:

XX:15:00

XX:30:00

XX:45:00

XX:00:00

10.9.2	TDSP Metered Entities

IDR meters used for settlement of TDSP Metered Entities shall:

(1)	Capture energy consumption in increments consistent with, or in fractions of, ERCOT-defined settlement time interval;

(2)	Provide interval data on a schedule that supports the requirements of final settlement;

(3)	Have battery or other energy-storage back-up to maintain time during power outages;

(4)	Have time synchronization capability;

(5)	Maintain meter clocks on a time reference that enables the TDSP to submit data on the Central Prevailing Time.  The meter clock shall be synchronized to within at least +/- five percent (5%) of the Settlement Interval when compared to the National Institute of Standards and Technology (NIST) Atomic Clock;

(6)	Have data aggregated to the appropriate Settlement Interval time block by the TDSP prior to the data being sent to ERCOT if recorded at increments less than the ERCOT defined settlement interval;

(7)	Be able to capture energy in increments of five (5) minutes (excluding memory allocation) for new and replacement IDR meters used for settlement;

(8)	Divide each hour into Settlement Intervals ending as follows:

XX:15:00

XX:30:00

XX:45:00

XX:00:00

(9)	IDR data submitted to ERCOT for Operating Days January 1, 2003, or later must contain only whole days with start times beginning at 0000 and stop times ending at 2359.

10.9.3	Failure to Comply with Standards

If the TDSP fails to comply with the standards for EPS Metering Facilities referred to in this Section and the SMOG, then ERCOT shall notify the PUCT or the appropriate Governmental Authority.

10.10	Security of Meter Data

10.10.1	ERCOT Polled Settlement Meters

TDSP’s are responsible for data security of the EPS Metering Facilities on their system.  This responsibility extends to third-party contracts and access to EPS Metering Facilities.

TDSPs or any Entity authorized to poll EPS Meters may not issue any EPS Meter programming passwords to any Market Participant.

10.10.1.1	TDSP Data Security Responsibilities

The TDSP shall:

(1)	Maintain and modify the passwords for programming and read access to EPS Meters;

(2)	Provide the appropriate password access to ERCOT, which will allow ERCOT to synchronize the meter clock;

(3)	Establish any other security requirements for accessing the EPS Meters so as to ensure the security of those meters and their meter data;

(4)	Coordinate any EPS Meter programming parameter changes with ERCOT according to this Section, including informing the Load or Resource Entity of any changes to the meter;

(5)	Upon request of the Resource Entity that represents an EPS metered Facility, provide the EPS meter “read only” password to such Resource Entity for such Facility and other EPS metered Facility required to calculate their QSE Load, to the extent that such provision does not violate the customer service and protection provisions of the PUCT Substantive Rules; and

(6)	Modify the “read only” password for EPS meters when a Resource Entity that represents a Facility requests a change due to data security reasons, provided that such modification does not violate the customer service and protection provisions of the PUCT Substantive Rules.

10.10.1.2	ERCOT Data Security Responsibilities

ERCOT may request that the TDSP alter the password and other requirements for accessing EPS Meters, as it deems necessary.

10.10.1.3	Resource Entity Data Security Responsibilities

A Resource Entity must request that the TDSP modify the EPS Meter read only password for a Facility when the Resource Entity relationships that affect EPS Meter data security change.  Such request must include the reason for the request.

10.10.1.4	Third Party Access Withdrawn

If, in the reasonable opinion of ERCOT, access granted to a third party interferes with or impedes ERCOT’s ability to poll any EPS Meter, ERCOT may require immediate withdrawal of any access granted to such third party.  Separate access through additional communications ports may be allowed so long as it does not interfere with ERCOT’s ability to communicate with the meter.

10.10.1.5	Meter Site Security

EPS Metering Facilities and secondary devices that could have any impact on the performance of the EPS Metering Facilities must be sealed to the extent practicable.

ERCOT shall provide TDSPs with uniquely numbered seals to be used by the TDSP EPS Meter Inspector to seal EPS Meters and EPS Meter test switches.  Procedures for seal use shall be in accordance with this Section and the SMOG.

10.10.2	TDSP Metered Entities

Security for TDSP polled meters and meter data shall be the responsibility of the TDSP.  Each TDSP shall maintain polled meters in accordance with applicable Governmental Authority rules and regulations.  The TDSP shall ensure that only Customer-approved Market Participants have access to the Customer meter.

10.11	Validating, Editing, and Estimating of Meter Data

10.11.1	ERCOT Polled Settlement Meters

The raw meter data that ERCOT retrieves from EPS Meters must be processed by MDAS using the Validating, Editing, and Estimating (VEE) procedures published in Section 11, Data Acquisition and Aggregation, and the SMOG in order to produce Settlement Quality Meter Data. During periods for which no primary EPS Meter data is available, ERCOT shall use the backup meter data or substitute estimated usage data for that metered Entity using estimation procedures referred to in these Protocols and the SMOG.  This data shall be used by ERCOT in its settlement and billing process.

10.11.2	Obligation to Assist

At the request of ERCOT, TDSPs and Market Participants shall promptly assist ERCOT in correcting or replacing defective data from EPS Meters and in detecting and correcting underlying causes for such defects.  Such assistance shall be rendered in a timely manner so that the settlement process is not delayed.

10.11.3	TDSP Settlement Meters

The TDSP shall provide ERCOT with Settlement Quality Meter Data for the TDSP Settlement Meters on its system and shall ensure that at a minimum the VEE requirements as specified in the Uniform Business Practices (UBP) standard for Validating, Editing, and Estimating have been properly performed on such data.  ERCOT shall not perform any VEE on the Settlement Quality Meter Data it receives from TDSPs.

The following UBP manual validation processes are exempt for Interval Data:

(1)	Spike Check; and

(2)	Reactive channel check for kWh data

10.12	Communications

10.12.1	ERCOT Acquisition of Meter Data

ERCOT shall acquire meter data via the following communication links:

(1)	ERCOT private communication network established by ERCOT for ERCOT Real-Time metered Entities; and

(2)	Standard voice telephone circuit or other ERCOT-approved communication technology provided by the TDSP for EPS Meters.

10.12.2	TDSPs Meter Data Submittal to ERCOT

TDSPs shall submit meter consumption data to ERCOT through a standard data interface into the MDAS.  In order to submit meter consumption data, TDSPs shall use an automated system with an ERCOT approved and tested interface to MDAS.

10.12.3	ERCOT Distribution of Settlement Meter Data

ERCOT shall distribute Settlement Quality Meter Data to Market Participants via:

(1)	MIS Pass-Through – When TDSP submits meter consumption data to ERCOT, information pertaining to specific Market Participants shall be removed and automatically forwarded on to that specific Market Participant (i.e., a CR will automatically receive the meter consumption data and other information for the ESI ID’s that the CR represented during the meter data timeframe.); and

(2)	On Request – A Market Participant may submit an electronic request via the MIS for specific meter consumption data.  ERCOT will receive and validate the request and, if appropriate, automatically forward the appropriate information to the Market Participant.

10.13	Meter Identification

The device id used to identify an EPS Meter shall be unique for such meters on the ERCOT System.  ERCOT shall maintain a master list of device ids and shall notify each TDSP if the device id selected has been used elsewhere in MDAS.

10.14	Exemptions from Compliance to Metering Protocols

10.14.1	Authority to Grant Exemptions

ERCOT may grant on a case by case basis, exemptions from compliance on a temporary basis until new arrangements can be completed in accordance with the guidelines as listed below.  Any permanent exemption to this Section requires approval by the Technical Advisory Committee (TAC).  Any permanent exemption shall be subject to periodic review and revocation by TAC.

10.14.2	Guidelines for Granting Temporary Exemptions

ERCOT shall use the following process when considering applications for temporary exemptions from compliance with this Section and the SMOG.

(1)	Publication of Guidelines:  ERCOT shall post on the MIS the general guidelines that it will use when considering applications for exemptions within one (1) week of a change of guidelines, so as to achieve consistency in its reasoning and decision-making and to give prospective applicants an indication of whether an application for exemption may be considered favorably.

(2)	Publication of Decision:  ERCOT shall post on the MIS the application for exemption and whether the application was approved or rejected by ERCOT and the reasons for rejecting the application, if applicable, on a quarterly basis.

10.14.3	Procedure for Applying for Exemptions

All applications to ERCOT for exemptions from compliance with the requirements of this Section must be submitted in writing.  ERCOT shall confirm receipt of an application within three (3) Business Days of receipt.  For temporary exemptions, ERCOT shall decide whether to grant or reject the exemption within forty-five (45) Business Days of receipt.  For permanent exemptions, ERCOT shall forward the application to TAC for review at the next scheduled meeting for which appropriate Notice can be made.  At any time during the application process, ERCOT may require the applicant to provide additional information in support of its application.

The applicant shall provide such additional information to ERCOT within five (5) Business Days of receiving the request or within such other period as ERCOT may specify.  If ERCOT requests additional information more than forty (40) Business Days after the date on which it received the application, ERCOT shall have an additional seven (7) Business Days after receiving that additional information in which to consider the application.  If the applicant does not provide the additional information requested, then ERCOT shall reject the application, in which case it will notify the applicant that its application has been rejected for failure to provide the additional information.

10.14.3.1	Information to be Included in the Application

The application for exemption to ERCOT shall include:

(1)	A detailed description of the exemption sought, including specific reference to the relevant Section(s) of these Protocols or the SMOG authorizing ERCOT to grant the exemption, and the Metering Facilities to which the exemption will apply;

(2)	A detailed statement of the reason for seeking the exemption, including any supporting documentation;

(3)	Details of the Entity(s) to which the exemption will apply;

(4)	Details of the location to which the exemption will apply;

(5)	Details of the period of time for which the exemption will apply, including the proposed start and finish dates of that period; and

(6)	Any other information requested by ERCOT.